## Assumptions Summary
2020-2021 Location-Based Forecasts
This workbook presents the IGP location-based forecasts. The Scenarios worksheet describes the DBESS, DGPV, EE, and EV load layers that correspond to each scenario. The forecasts include the Base Load, DGPV, DBESS, Managed EV Charging, Energy Efficiency, and the Forecasted Load Growth for Scenario 2.
Version History
Date | Version | Description
2021-10-08 | 1 | First Release of the Draft Location-Based Forecasts Workbooks
Worksheet Descriptions
Worksheet | Category | Description | Source
Assumptions Summary | Assumptions Summary | Includes Workbook Version History, Worksheet Descriptions, and References | HECO
Glossary | Glossary | Definitions of All Acronyms and Common Terms Used in the Workbook | HECO
References | References | Provides Links to All Pertinent and Related Documents and Workbooks | HECO
Scenarios | Scenarios | Scenarios for Current Exisiting Modeling Cases | HECO
Demand Forecast by Circuit | Demand Forecast | Demand Forecast by Circuit Base Forecast | HECO
Demand Forecast by Transformer |  | Demand Forecast by Substation Transformer Base Forecast | HECO
DBESS Forecast | DER Forecasts | Distributed Battery Energy Storage Systems (DBESS) Base Forecast | HECO
DGPV Forecast |  | Distributed Generation Photovoltaic Systems (DGPV) Base Forecast | HECO
Energy Efficiency Forecast | Energy Efficiency Forecast | Energy Efficiency (EE) Base Forecast | HECO
Unmanaged EV Charging | Unmanaged EV Forecast | Unmanaged Electric Vehicle (EV) Charging Base Forecast | HECO
Forecasted Load Growth | Other Base Load Forecasts | Forecasted Load Growth Base Forecast | HECO
Base Load |  | Base Load | HECO

## Glossary
Glossary |  | Return to Assumptions Summary
Acronym/ Terminology | Definition
8760 | 365 days/year x 24 hours/day = 8760 hours/year
Base Load | Created using historical load data and serves as the basis for creating the location-based forecasts
CBRE Phase 2 Small Projects | Community Based Renewable Energy Phase 2 small projects < 250 kW
CGS | Customer Grid Supply
CGS+ | Customer Grid Supply Plus
Conductor Overload Violation | Circuit condition exceeding thermal rating of conductors
CSS | Customer Self Supply
DBESS | Distributed Battery Energy Storage System
DER | Distributed Energy Resources
DER/BESS | Combined DER and DBESS
DGPV | Distributed Generation Photovoltaics
DR | Demand Response
EDR | Emergency Demand Response
EE | Energy Efficiency
EoT | Electrification of Transportation
EV | Electric Vehicle
Executed DER | DER that has been installed and energized on the system
Fct | Forecast, Forecasted
FIT | Feed-In Tariff
Gross Load | Load Without the Impacts of DER
Historical Peak Demand | Peak load determined using the historical data for the circuit or transformer
LDV | Light Duty Vehicle
LTC | Load Tap Changer
Managed Charging | Charging during hours of higher renewable penetration and lower system cost through rates and/or demand response (DR) programs
MVA | Megavolt-amperes. Unit of Apparent Power
MW | Megawatt, Unit of Real Power/ Capacity
NEM | Net Energy Metering
NEM+ | Net Energy Metering Plus
Net Load | Underlying Load Plus the Impacts of DGPV, DBESS, EE, and EV, Load Layers
PPA | Power Purchase Agreement
PV | Utility-scale Photovoltaic Generator
Rating | Represents the Assumed Power (MW) Produced in Every Hour
Schedule-G | General Service Non-Demand Rate (Small Commercial Customer)
Schedule-J | General Service Demand Rate (Medium Commercial Customer)
Schedule-P | Large Power Service Rate (Large Commercial Customer)
Schedule-R | Residential Service Rate (Residential Customer)
SE | Smart Export
Service Requests | Request for electrical service including location and estimated demand information
SIA | Standard Interconnection Agreement
Solar | Utility-scale Photovoltaic Generator
Total Anticipated DER | Executed DER + Forecasted DER
Underlying Load | Load based on customer-level sales forecast
Voltage Violation | Circuit condition where voltage exceeds (low and/or high) tariff limits

## References
References |  | Return to Assumptions Summary
Source | Materials
Revised Draft IGP Inputs and Assumptions Document, August 3, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/20210803_heco_submittal_of_igp_inputs_and_assum_and_der_hosting_capacity.pdf
Revised Draft IGP Inputs and Assumptions Document, August 19, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/stakeholder_engagement/working_groups/forecast_assumptions/20210819_heco_submittal_of_revised_igp_inputs_and_assumptions.pdf
Revised Draft Oahu IGP Inputs and Assumptions Workbooks 3, August 3, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/Revised%202021-08-03%20Draft%20Oahu%20Inputs%20Workbook%203.xlsx
Revised Draft Oahu IGP Inputs and Assumptions Workbooks 4, August 3, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/Revised%202021-08-03%20Draft%20Oahu%20Inputs%20Workbook%204.xlsx
Revised Draft Hawaii IGP Inputs and Assumptions Workbooks 3, August 3, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/Revised%202021-08-03%20Draft%20Hawaii%20Island%20Inputs%20Workbook%203.xlsx
Revised Draft Hawaii IGP Inputs and Assumptions Workbooks 4, August 3, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/Revised%202021-08-03%20Draft%20Hawaii%20Island%20Inputs%20Workbook%204.xlsx
Revised Draft Maui IGP Inputs and Assumptions Workbooks 3, August 3, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/Revised%202021-08-03%20Draft%20Maui%20Inputs%20Workbook%203.xlsx
Revised Draft Maui IGP Inputs and Assumptions Workbooks 4, August 3, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/Revised%202021-08-03%20Draft%20Maui%20Inputs%20Workbook%204.xlsx
Revised Draft Molokai IGP Inputs and Assumptions Workbooks 3, August 3, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/Revised%202021-08-03%20Draft%20Molokai%20Inputs%20Workbook%203.xlsx
Revised Draft Molokai IGP Inputs and Assumptions Workbooks 4, August 3, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/Revised%202021-08-03%20Draft%20Molokai%20Inputs%20Workbook%204.xlsx
Revised Draft Lanai IGP Inputs and Assumptions Workbooks 3, August 3, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/Revised%202021-08-03%20Draft%20Lanai%20Inputs%20Workbook%203.xlsx
Revised Draft Lanai IGP Inputs and Assumptions Workbooks 4, August 3, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/Revised%202021-08-03%20Draft%20Lanai%20Inputs%20Workbook%204.xlsx
Revised Draft IGP Inputs and Assumptions Document, March 30, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/stakeholder_engagement/working_groups/forecast_assumptions/20210330_wg_fa_deliverable_draft.pdf
Revised Draft IGP Grid Needs Assessment & Solution Evaluation Methodology Document, March 30, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/stakeholder_engagement/working_groups/solution_evaluation_and_optimization/20210330_wg_seo_deliverable_draft.pdf
IGP DER Forecast - Oahu, January 29, 2020 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/stakeholder_engagement/working_groups/forecast_assumptions/HE_DER_forecast_IGP.xlsx
IGP DER Forecast - Hawaii, January 29, 2020 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/stakeholder_engagement/working_groups/forecast_assumptions/HL_DER_forecast_IGP.xlsx
IGP DER Forecast - Maui (Maui BESS Included from Slide 31), January 29, 2020 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/stakeholder_engagement/working_groups/forecast_assumptions/ME_DER_forecast_IGP.xlsx
Distribution Planning Methodology | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/stakeholder_engagement/working_groups/distribution_planning/20200602_dpwg_distribution_planning_methodology.pdf

## Scenarios
|  |  | Forecast Types |  |  |  | Return to Assumptions Summary
No. | Modeling Case | Purpose | DER Forecast | EV Forecast | EE Forecast | TOU Load Shape
1 | Base | Reference Case | Base Forecast | Base Forecast | Base Forecast | Managed EV Charging
2 | High Load Customer Technology Adoption Bookend | Understand the impact of customer adoption of technologies for DER, electric vehicles, energy efficiency, and time-of-use rates that lead to higher loads. | Low Forecast | High Forecast | Low Forecast | Unmanaged EV Charging
3 | Low Load Customer Technology Adoption Bookend | Understand the impact of customer adoption of technologies for DER, electric vehicles, energy efficiency, and time-of-use rates that leads to lower loads. | High Forecast | Low Forecast | High Forecast | Managed EV Charging

## Demand Forecast by Circuit
Return to Assumptions Summary
Demand Forecast by Circuit - High Load Customer Technology Adoption Bookend
The Demand Forecast by Circuit shows the net peak forecast by year in megawatts (MW) for each circuit for 2021-2030. For Lanai, this forecast is the sum of the Base Load, Distributed Battery Energy Storage Systems (DBESS), Distributed Generation Photovoltaic Systems (DGPV), Energy Efficiency (EE), Electric Vehicle (EV), and the Forecasted Load Growth layers. The corresponding substation transformer that feeds each distribution circuit is shown. The Equipment Rating (MVA) is the thermal rating under normal conditions of the main conductor out of the substation.
Demand Forecast Peak (MW)
Substation Transformer | Circuit | Equipment Rating (MVA) | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Miki Basin PP | 1208 | 11.1233 | 0.15441 | 0.14846 | 0.13471 | 0.13478 | 1.444 | 1.4418 | 1.4347 | 1.4332 | 1.4297 | 1.4217
Miki Basin PP | 1210 | 11.1233 | 2.217 | 2.175 | 2.0811 | 2.0789 | 2.3305 | 2.3134 | 2.2638 | 2.2509 | 2.225 | 2.1692
Miki Basin PP | 1212 | 11.1233 | 2.4049 | 2.3925 | 2.3711 | 2.3651 | 2.3573 | 2.3486 | 2.3346 | 2.3267 | 2.3164 | 2.301

## Demand Forecast by Transformer
Return to Assumptions Summary
Demand Forecast by Transformer - High Load Customer Technology Adoption Bookend
The Demand Forecast by Substation Transformer shows the demand forecast by year in megawatts (MW) for each substation transformer for 2021-2030. For Lanai, the forecast for each substation transformer is the sum of the Demand Forecast Peaks for each of the distribution circuits that are fed by that transformer. The Equipment Rating (MW) is the largest nameplate capacity rating of the substation transformer.
Demand Forecast Peak (MW)
Substation Transformer | Equipment Rating (MVA) | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Miki Basin PP | n/a | 4.7763 | 4.7159 | 4.5868 | 4.5788 | 6.1319 | 6.1038 | 6.0332 | 6.0108 | 5.9711 | 5.892

## DBESS Forecast
Return to Assumptions Summary
Distributed Battery Energy Storage Systems (DBESS) - Low Forecast
Distributed Energy Resources (DER) include Distributed Generation Photovoltaic (DGPV) and Distributed Battery Energy Storage Systems (DBESS). The DBESS Load layer represents the impacts of future behind the meter battery energy storage systems paired with PV systems in the DGPV Load layer for residential and commercial customers. The peak incremental amount added in megawatts (MW) to each distribution circuit per year for the DBESS Load layer is shown for 2021-2030.
Amount Added Per Year (MW)
Substation Transformer | Circuit | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Miki Basin PP | 1208 | -0.005785 | -0.0038756 | -0.0030249 | -0.0018905 | -0.0022686 | -0.0026467 | -0.0026467 | -0.0030249 | -0.003403 | -0.003403
Miki Basin PP | 1210 | -0.038527 | -0.025811 | -0.020145 | -0.012591 | -0.015109 | -0.017627 | -0.017627 | -0.020145 | -0.022663 | -0.022663
Miki Basin PP | 1212 | -0.0066875 | -0.0044802 | -0.0034968 | -0.0021855 | -0.0026226 | -0.0030597 | -0.0030597 | -0.0034968 | -0.0039338 | -0.0039338

## DGPV Forecast
Return to Assumptions Summary
Distributed Generation Photovoltaic Systems (DGPV) - Low Forecast
Distributed Energy Resources (DER) include Distributed Generation Photovoltaic Systems (DGPV) and Distributed Battery Energy Storage Systems (DBESS). The DGPV Load layer represents the impacts of future behind the meter PV for residential and commercial customers. This includes forecasted DGPV load for customers participating in Emergency Demand Response Program (EDRP) and in a future DER program, based on the Company's proposed, "Standard DER Tariff" and "Scheduled Dispatch Program". The peak incremental amount in megawatts (MW) added to each distribution circuit per year for the DGPV Load layer is shown for 2021-2030.
Amount Added Per Year (MW)
Substation Transformer | Circuit | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Miki Basin PP | 1208 | -0.0040835 | -0.0036298 | -0.01191 | -0.0022686 | -0.0027224 | -0.0046507 | -0.009982 | -0.0036298 | -0.0055582 | -0.010889
Miki Basin PP | 1210 | -0.027196 | -0.024174 | -0.079321 | -0.015109 | -0.018131 | -0.030973 | -0.066479 | -0.024174 | -0.037017 | -0.072522
Miki Basin PP | 1212 | -0.0047206 | -0.0041961 | -0.013768 | -0.0026226 | -0.0031471 | -0.0053763 | -0.011539 | -0.0041961 | -0.0064253 | -0.012588

## Energy Efficiency Forecast
Return to Assumptions Summary
Energy Efficiency (EE) - Low Forecast
The Energy Efficiency (EE) Load layer represents the impacts of future EE for both residential and commercial customers. The peak incremental amount in megawatts (MW) added to each distribution circuit per year for the EE Load layer is shown for 2021-2030.
Amount Added Per Year (MW)
Substation Transformer | Circuit | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Miki Basin PP | 1208 | -0.00040089 | -0.00040089 | -0.00040527 | -0.00043913 | -0.00049762 | -0.0004547 | -0.00042502 | -0.00044349 | -0.00045832 | -0.00044876
Miki Basin PP | 1210 | -0.0050373 | -0.0050373 | -0.0050924 | -0.0055178 | -0.0062527 | -0.0057135 | -0.0053405 | -0.0055726 | -0.0057589 | -0.0056388
Miki Basin PP | 1212 | -0.0059616 | -0.0059616 | -0.0060268 | -0.0065302 | -0.0074 | -0.0067619 | -0.0063205 | -0.0065952 | -0.0068156 | -0.0066734

## Unmanaged EV Charging
Return to Assumptions Summary
Unmanaged Electric Vehicle (EV) Charging - High Forecast
The Unmanaged Electric Vehicle (EV) Load layer represents the future electric light-duty vehicle (LDV) charging behavior without the impacts of Managed Charging. The peak incremental amount added in megawatts (MW) to each distribution circuit per year for the EV Load layer by circuit is shown for 2021-2030.
Amount Added Per Year (MW)
Substation Transformer | Circuit | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Miki Basin PP | 1208 | 0.0019489 | 0.0019489 | 0.0015972 | 0.0046645 | 0.0046741 | 0.0055849 | 0.0059847 | 0.0055437 | 0.0059442 | 0.0067612
Miki Basin PP | 1210 | 0.012979 | 0.012979 | 0.010637 | 0.031065 | 0.031129 | 0.037195 | 0.039857 | 0.03692 | 0.039587 | 0.045029
Miki Basin PP | 1212 | 0.0022529 | 0.0022529 | 0.0018463 | 0.0053922 | 0.0054033 | 0.0064562 | 0.0069184 | 0.0064086 | 0.0068715 | 0.007816

## Forecasted Load Growth
Return to Assumptions Summary
Forecasted Load Growth
The Forecasted Load Growth layer represents the future increases in the Underlying Load layer and known service requests for residential and commercial customers. The peak incremental amount added in megawatts (MW) to each distribution circuit per year for the Forecasted Load Growth layer is shown for 2021-2030.
Amount Added Per Year (MW)
Substation Transformer | Circuit | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Miki Basin PP | 1208 | 0 | 0 | 0 | 0 | 1.31 | 0 | 0 | 0 | 0 | 0
Miki Basin PP | 1210 | 0.23 | 0 | 0 | 0 | 0.26 | 0 | 0 | 0 | 0 | 0
Miki Basin PP | 1212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Base Load
Return to Assumptions Summary
Base Load
The Base Load layer represents the starting point for each circuit forecast. This layer is developed based on the circuit historical peak demands. The base load is shown in megawatts (MW) for each distribution circuit.
Substation Transformer | Circuit | Base Load (MW)
Miki Basin PP | 1208 | 0.16273
Miki Basin PP | 1210 | 2.0448
Miki Basin PP | 1212 | 2.42