## Assumptions Summary
2020-2021 Distribution DER Hosting Capacity Grid Needs High DER Forecast
This workbook presents the IGP Distribution DER Hosting Capacity Grid Needs Report Tables; the DER growth and the hosting capacity analysis results. The Scenarios worksheet describes the DGPV forecast that corresponds to each scenario.
Version History
Date | Version | Description
2021-08-03 | 1 | First Release of the Draft Distribution DER Hosting Capacity Grid Needs Report Tables from the August 2021 Update. --Based on Corporate Forecast from March 2021
2021-11-05 | 2 | Distribution DER Hosting Capacity Grid Needs Report Tables from the November 2021 Update. --Based on Corporate Forecast from the August Update (submitted August 19, 2021). Includes the Base DER forecast sensitivity.
Worksheet Descriptions
Worksheet | Category | Description | Source
Assumptions Summary | Assumptions Summary | Includes Workbook Version History, Worksheet Descriptions, and References | HECO
Glossary | Glossary | Definitions of All Acronyms and Common Terms Used in the Workbook | HECO
References | References | Provides Links to All Pertinent and Related Documents and Workbooks | HECO
Scenarios | Scenarios | Scenarios for Current Exisiting Modeling Cases | HECO
Oahu DER Growth | Adjusted DER Growth by Island | O‘ahu Adjusted DER Growth - Base Forecast | HECO
Hawaii Island DER Growth |  | Hawai‘i Island Adjusted DER Growth - Base Forecast | HECO
Maui Island DER Growth |  | Maui Island Adjusted DER Growth - Base Forecast | HECO
Lanai DER Growth |  | Lana‘I Adjusted DER Growth - Base Forecast | HECO
Molokai DER Growth |  | Moloka‘i Adjusted DER Growth - Base Forecast | HECO
Oahu Circuit DER Growth | Adjusted DER Growth by Circuit | O‘ahu Adjusted DER Growth by Circuit - Base Forecast | HECO
Hawaii Island Circuit DER Growth |  | Hawai‘i Island Adjusted DER Growth by Circuit - Base Forecast | HECO
Maui Total DER Growth |  | Maui Island Adjusted DER Growth by Circuit - Base Forecast | HECO
Lanai Circuit DER Growth |  | Lana‘I Adjusted DER Growth by Circuit - Base Forecast | HECO
Molokai Circuit DER Growth |  | Moloka‘i Adjusted DER Growth by Circuit - Base Forecast | HECO
Summary HC Results | Hosting Capacity Results | Summary of Hosting Capacity Results (All Islands) - Base Forecast | HECO
O‘ahu HC Results |  | O‘ahu Hosting Capacity Analysis Results by Circuit - Base Forecast | HECO
Hawai‘i Island HC Results |  | Hawai‘i Island Hosting Capacity Analysis Results by Circuit - Base Forecast | HECO
Maui Island HC Results |  | Maui Island Hosting Capacity Analysis Results by Circuit - Base Forecast | HECO
Lana‘i HC Results |  | Lana‘i Hosting Capacity Analysis Results by Circuit - Base Forecast | HECO
Moloka‘i HC Results |  | Moloka‘i Hosting Capacity Analysis Results by Circuit - Base Forecast | HECO
O‘ahu Total DER | DER Growth by Circuit and Hosting Capacity | O‘ahu Total DER Growth by Circuit; Executed and Updated Hosting Capacity - Base Forecast | HECO
Hawai‘i Island Total DER |  | Hawai‘i Island Total DER Growth by Circuit; Executed and Updated Hosting Capacity - Base Forecast | HECO
Maui Island Total DER |  | Maui Total DER Growth by Circuit; Executed and Updated Hosting Capacity - Base Forecast | HECO
Lana‘i Total DER |  | Lana‘i Total DER Growth by Circuit; Executed and Updated Hosting Capacity - Base Forecast | HECO
Moloka‘i Total DER |  | Moloka‘i Total DER Growth by Circuit; Executed and Updated Hosting Capacity - Base Forecast | HECO
Summary GNA | Grid Needs Assessment Results | Summary of Grid Needs Assessment Results (All Islands) - Base Forecast | HECO
O‘ahu GNA |  | O‘ahu Grid Needs Assessment Results by Circuit - Base Forecast | HECO
Hawai‘i Island GNA |  | Hawai‘i Island Grid Needs Assessment Results by Circuit - Base Forecast | HECO
Maui Island GNA |  | Maui Grid Needs Assessment Results by Circuit - Base Forecast | HECO
Lana‘i GNA |  | Lana‘i Grid Needs Assessment Results by Circuit - Base Forecast | HECO
Moloka‘i GNA |  | Moloka‘i Grid Needs Assessment Results by Circuit - Base Forecast | HECO

## Glossary
Glossary |  | Return to Assumptions Summary
Acronym/ Terminology | Definition
8760 | 365 days/year x 24 hours/day = 8760 hours/year
Base Load | Created using historical load data and serves as the basis for creating the location-based forecasts
CBRE Phase 2 Small Projects | Community Based Renewable Energy Phase 2 small projects < 250 kW
CGS | Customer Grid Supply
CGS+ | Customer Grid Supply Plus
Conductor Overload Violation | Circuit condition exceeding thermal rating of conductors
CSS | Customer Self Supply
DBESS | Distributed Battery Energy Storage System
DER | Distributed Energy Resources
DER/BESS | Combined DER and DBESS
DGPV | Distributed Generation Photovoltaics
DR | Demand Response
EDR | Emergency Demand Response
EE | Energy Efficiency
EoT | Electrification of Transportation
EV | Electric Vehicle
Executed DER | DER that has been installed and energized on the system
Fct | Forecast, Forecasted
FIT | Feed-In Tariff
Gross Load | Load Without the Impacts of DER
Historical Peak Demand | Peak load determined using the historical data for the circuit or transformer
LDV | Light Duty Vehicle
LTC | Load Tap Changer
Managed Charging | Charging during hours of higher renewable penetration and lower system cost through rates and/or demand response (DR) programs
MVA | Megavolt-amperes. Unit of Apparent Power
MW | Megawatt, Unit of Real Power/ Capacity
NEM | Net Energy Metering
NEM+ | Net Energy Metering Plus
Net Load | Underlying Load Plus the Impacts of DGPV, DBESS, EE, and EV, Load Layers
PPA | Power Purchase Agreement
PV | Utility-scale Photovoltaic Generator
Rating | Represents the Assumed Power (MW) Produced in Every Hour
Schedule-G | General Service Non-Demand Rate (Small Commercial Customer)
Schedule-J | General Service Demand Rate (Medium Commercial Customer)
Schedule-P | Large Power Service Rate (Large Commercial Customer)
Schedule-R | Residential Service Rate (Residential Customer)
SE | Smart Export
Service Requests | Request for electrical service including location and estimated demand information
SIA | Standard Interconnection Agreement
Solar | Utility-scale Photovoltaic Generator
Total Anticipated DER | Executed DER + Forecasted DER
Underlying Load | Load based on customer-level sales forecast
Voltage Violation | Circuit condition where voltage exceeds (low and/or high) tariff limits

## References
References |  | Return to Assumptions Summary
Source | Materials
Distribution DER Hosting Capacity Grid Needs Report August 3, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/distribution_der_hosting_capacity_grid_needs_03Aug2021.pdf
Distribution DER Hosting Capacity Grid Needs Report Tables August 3, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/Distribution%20DER%20Hosting%20Capacity%20Grid%20Needs%2003Aug2021%20Report%20Tables.xlsx
Distribution Planning Methodology | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/stakeholder_engagement/working_groups/distribution_planning/20200602_dpwg_distribution_planning_methodology.pdf
Revised Draft IGP Inputs and Assumptions Document, August 3, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/20210803_heco_submittal_of_igp_inputs_and_assum_and_der_hosting_capacity.pdf
Revised Draft IGP Inputs and Assumptions Document, August 19, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/stakeholder_engagement/working_groups/forecast_assumptions/20210819_heco_submittal_of_revised_igp_inputs_and_assumptions.pdf
Distribution DER Hosting Capacity Grid Needs Report October 2021 Update | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/20211008_distribution_der_hosting_capacity_grid_needs_draft.pdf
Distribution DER Hosting Capacity Grid Needs Report Tables October 8, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/Revised%202021-10-08%20Distribution%20DER%20Hosting%20Capacity%20Grid%20Needs%20High%20Forecast.xlsx

## Scenarios
|  |  | Forecast Types | Return to Assumptions Summary
No. | Modeling Case | Purpose | DER Forecast
1 | Base | Reference Case | Base Forecast
2 | High Load Customer Technology Adoption Bookend | Understand the impact of customer adoption of technologies for DER, electric vehicles, energy efficiency, and time-of-use rates that lead to higher loads. | Low Forecast
3 | Low Load Customer Technology Adoption Bookend | Understand the impact of customer adoption of technologies for DER, electric vehicles, energy efficiency, and time-of-use rates that leads to lower loads. | High Forecast

## Oahu DER Growth
Return to Assumptions Summary
O‘ahu Adjusted DER Growth - Base Forecast
The Adjusted DER Growth shows the annual DER corporate forecast and the adjustments made to account for projects not included in the corporate forecast. Adjustments are included for CBRE Phase 2 small projects or pending known large projects (such as CBRE Phase 1, FIT, and large SIA (> 250 kW)). The forecast is shown by system peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth
Forecasted DER Growth
Year | Corporate DER Forecast (Cumulative kW) | Adjustment for CBRE Phase 2 Small Projects (Cumulative kW) | Adjustment for Large Projects (Cumulative kW) | Adjusted DER Growth (Incremental kW)
kW | A | B | C | D = (A+B+C)1 - (A+B+C)0
2020 | 534703.6864 | 0 | 0 | n/a
2021 | 578149.5645 | 6000 | 29822 | 79267.8781
2022 | 644016.9645 | 12000 | 35025 | 77070.4
2023 | 681380.9645 | 18000 | 35025 | 43364
2024 | 701906.9645 | 24000 | 39694 | 31195
2025 | 723233.9645 | 30000 | 39694 | 27327

## Hawaii Island DER Growth
Return to Assumptions Summary
Hawai‘i Island Adjusted DER Growth - Base Forecast
The Adjusted DER Growth shows the annual DER corporate forecast and the adjustments made to account for projects not included in the corporate forecast. Adjustments are included for CBRE Phase 2 small projects or pending known large projects (such as CBRE Phase 1, FIT, and large SIA (> 250 kW)). The forecast is shown by system peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth
Forecasted DER Growth
Year | Corporate DER Forecast (Cumulative kW) | Adjustment for CBRE Phase 2 Small Projects (Cumulative kW) | Adjustment for Large Projects (Cumulative kW) | Adjusted DER Growth (Incremental kW)
kW | A | B | C | D = (A+B+C)1 - (A+B+C)0
2020 | 110107.527 | 0 | 0 | n/a
2021 | 118085.997 | 1500 | 850 | 10328.47
2022 | 124018.097 | 3000 | 850 | 7432.1
2023 | 130519.117 | 4500 | 850 | 8001.02
2024 | 134421.137 | 6000 | 850 | 5402.02
2025 | 138801.157 | 7500 | 850 | 5880.02

## Maui Island DER Growth
Return to Assumptions Summary
Maui Island Adjusted DER Growth - Base Forecast
The Adjusted DER Growth shows the annual DER corporate forecast and the adjustments made to account for projects not included in the corporate forecast. Adjustments are included for CBRE Phase 2 small projects or pending known large projects (such as CBRE Phase 1, FIT, and large SIA (> 250 kW)). The forecast is shown by system peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth
Forecasted DER Growth
Year | Corporate DER Forecast (Cumulative kW) | Adjustment for CBRE Phase 2 Small Projects (Cumulative kW) | Adjustment for Large Projects (Cumulative kW) | Adjusted DER Growth (Incremental kW)
kW | A | B | C | D = (A+B+C)1 - (A+B+C)0
2020 | 119232.3133 | 0 | 0 | n/a
2021 | 129448.525 | 1695 | 1750 | 13661.2118
2022 | 138585.525 | 3390 | 1750 | 10832
2023 | 147328.525 | 5085 | 1750 | 10438
2024 | 152757.6072 | 6780 | 1750 | 7124.0822
2025 | 158259.6894 | 8475 | 1750 | 7197.0822

## Lanai DER Growth
Return to Assumptions Summary
Lana‘i Adjusted DER Growth - Base Forecast
The Adjusted DER Growth shows the annual DER corporate forecast and the adjustments made to account for projects not included in the corporate forecast. Adjustments are included for CBRE Phase 2 small projects or pending known large projects (such as CBRE Phase 1, FIT, and large SIA (> 250 kW)). The forecast is shown by system peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth
Forecasted DER Growth
Year | Corporate DER Forecast (Cumulative kW) | Adjustment for CBRE Phase 2 Small Projects (Cumulative kW) | Adjustment for Large Projects (Cumulative kW) | Adjusted DER Growth (Incremental kW)
kW | A | B | C | D = (A+B+C)1 - (A+B+C)0
2020 | 832.72 | 0 | 0 | n/a
2021 | 868.72 | 0 | 0 | 36
2022 | 900.72 | 0 | 0 | 32
2023 | 1005.72 | 0 | 0 | 105
2024 | 1025.72 | 0 | 0 | 20
2025 | 1049.72 | 0 | 0 | 24

## Molokai DER Growth
Return to Assumptions Summary
Moloka‘i Adjusted DER Growth - Base Forecast
The Adjusted DER Growth shows the annual DER corporate forecast and the adjustments made to account for projects not included in the corporate forecast. Adjustments are included for CBRE Phase 2 small projects or pending known large projects (such as CBRE Phase 1, FIT, and large SIA (> 250 kW)). The forecast is shown by system peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth
Forecasted DER Growth
Year | Corporate DER Forecast (Cumulative kW) | Adjustment for CBRE Phase 2 Small Projects (Cumulative kW) | Adjustment for Large Projects (Cumulative kW) | Adjusted DER Growth (Incremental kW)
kW | A | B | C | D = (A+B+C)1 - (A+B+C)0
2020 | 2678.3 | 0 | 0 | n/a
2021 | 2836.3 | 0 | 250 | 408
2022 | 2936.3 | 0 | 250 | 100
2023 | 3100.3 | 0 | 250 | 164
2024 | 3152.3 | 0 | 250 | 52
2025 | 3200.3 | 0 | 250 | 48

## Oahu Circuit DER Growth
Return to Assumptions Summary
O‘ahu Adjusted DER Growth by Circuit - Base Forecast
The Adjusted DER Growth by Circuit shows the annual DER growth by circuit. The forecast is shown by circuit (or feeder) peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth (kW)
Circuit | 2021 | 2022 | 2023 | 2024 | 2025
AALA | 77.491 | 246.79 | 87.181 | 60.506 | 44.299
AALAPAPA | 105.83 | 277.784 | 118.823 | 76.219 | 86.452
AHUA | 127.776 | 313.132 | 203.874 | 101.937 | 103.654
AHUI | 0 | 0 | 0 | 0 | 0
AIEA | 225.56 | 155.086 | 179.384 | 369.098 | 71.734
AIEA 2 | 20.745 | 39.835 | 36.976 | 7.228 | 20.881
AIEA 3 | 14.28 | 50.753 | 72.18 | 6.472 | 9.863
AINA KOA | 383.868 | 377.212 | 639.574 | 79.729 | 144.572
AINONI | 31.931 | 53.55 | 47.523 | 17.89 | 37.459
AIRPORT | 100 | 107.564 | 2.72 | 0 | 100
AIRPORT 1 | 0 | 0 | 0 | 100 | 0
AIRPORT 2 | 100 | 0 | 0 | 0 | 0
ALA MOANA | 0.637 | 100 | 100 | 0 | 100.637
ALEWA | 18.369 | 29.165 | 19.057 | 9.926 | 15.088
ALIAMANU | 336.932 | 208.848 | 295.632 | 168.832 | 65.977
ANOI | 194.913 | 267.354 | 146.295 | 58.059 | 51.377
ANUU | 68.093 | 369.408 | 87.431 | 199.344 | 400.622
ARCHER 1 | 100 | 100 | 100 | 0 | 100
ARCHER 2 | 200 | 300 | 100 | 100 | 0
ARCHER 3 | 401.768 | 552.433 | 417.504 | 200 | 511.786
ARCHER 4 | 0 | 200 | 0 | 0 | 0
AUDITORIUM | 117.3 | 316.872 | 121.09 | 4.218 | 11.248
BARBERS PT | 271.521 | 102.106 | 74.77 | 21.38 | 30.483
BAY DR | 63.286 | 40.09 | 32.8 | 5.452 | 9.337
BEACH LOTS | 240.332 | 488.115 | 276.505 | 316.902 | 183.127
BECKLEY | 8.399 | 32.611 | 6.95 | 5.717 | 6.781
BLACK PT | 9.283 | 27.366 | 5.095 | 9.389 | 7.455
BWS | 19.253 | 143.357 | 70.961 | 115.569 | 130.674
CARLOS LONG | 191.828 | 165.392 | 153.919 | 59.317 | 64.962
CASTNER | 205.88 | 331.335 | 222.246 | 194.765 | 149.621
CEIP 3 | 988 | 210.84 | 0 | 0 | 205.42
CEIP 4 | 77.107 | 67.985 | 78.213 | 19.732 | 36.306
CKT 10 | 0 | 237.785 | 0 | 0 | 0
CKT 12 | 0 | 100 | 0 | 0 | 0
CKT 16 | 4374 | 601.398 | 101.398 | 200 | 100
CKT 18 | 221.003 | 245.165 | 36.69 | 23.656 | 217.517
CKT 6 | 0 | 19.74 | 0 | 0 | 0
CKT 7 | 139.019 | 448.687 | 36.376 | 19.512 | 25.764
CKT 8 | 0 | 0 | 0 | 0 | 0
COCONUT GROVE | 55.164 | 145.4 | 49.932 | 8.986 | 26.76
DAIRYMENS | 40.456 | 60.274 | 43.381 | 19.812 | 17.362
DE RUSSY | 200 | 400 | 0 | 0 | 0
DEPOT RD | 104.863 | 217.006 | 137.087 | 67.633 | 66.388
DIAMOND HEAD | 422.045 | 284.509 | 441.479 | 419.22 | 127.397
DOLE 1 | 0 | 2.328 | 3.03 | 0 | 0
EKEKELA | 25.002 | 46.963 | 38.216 | 17.641 | 22.07
ENA 1 | 23.272 | 128.931 | 24.72 | 112.879 | 16.466
ENA 2 | 0 | 7.765 | 0 | 0 | 0
ENCHANTED LAKES | 142.129 | 371.514 | 251.876 | 164.892 | 65.693
EWA BEACH 1 | 450.415 | 637.23 | 459.988 | 185.363 | 283.986
EWA BEACH 2 | 214.663 | 434.434 | 204.892 | 324.409 | 69.832
EWA BEACH 3 | 259.105 | 455.113 | 384.51 | 127.638 | 99.149
EWA BEACH 4 | 254.659 | 858.107 | 320.755 | 123.991 | 181.475
EWA NUI 1 | 348.704 | 508.967 | 294.25 | 85.406 | 172.646
EWA NUI 2 | 705.29 | 468.926 | 451.671 | 496.766 | 577.137
FARMERS RD | 147.815 | 49.364 | 43.789 | 108.99 | 48.647
FORT ST | 109.728 | 6.386 | 3.444 | 2.012 | 3.181
FORT ST 1 | 100 | 100 | 100 | 0 | 0
FORT ST 2 | 23.937 | 107.775 | 111.135 | 5.635 | 5.385
FORT ST 3 | 6.538 | 101.226 | 0.922 | 0 | 0.922
FORT ST 4 | 34.625 | 91.437 | 108.936 | 30.145 | 20.577
FORT WEAVER 1 | 231.108 | 345.298 | 240.565 | 136.36 | 242.773
FORT WEAVER 2 | 379.495 | 461.625 | 332.806 | 183.147 | 306.197
FORT WEAVER 3 | 358.282 | 364.387 | 352.679 | 84.778 | 131.193
FORT WEAVER 4 | 234.213 | 216.554 | 191.995 | 84.709 | 81.855
HAHAIONE | 178.182 | 246.506 | 128.291 | 145.56 | 48.854
HALA 1 | 536.968 | 73.169 | 52.566 | 42.82 | 36.956
HALA 2 | 53.186 | 209.103 | 64.068 | 42.607 | 38.23
HALA 3 | 305.796 | 374.853 | 242.341 | 137.902 | 469.263
HALA 4 | 254.076 | 62.691 | 67.537 | 30.166 | 34.36
HALAWA | 159.299 | 107.883 | 70.752 | 24.252 | 34.156
HALEKOU | 249.75 | 185.208 | 143.129 | 76.823 | 50.988
HANUA 1 | 0 | 0 | 0 | 0 | 0
HANUA 2 | 0 | 0 | 0 | 0 | 0
HAUULA | 4966.497 | 99.219 | 116.411 | 63.189 | 54.114
HAWN PINE | 666 | 112.57 | 200 | 101.19 | 136.087
HAWN VILLAGE 1 | 100 | 1.052 | 0 | 100 | 0
HAWN VILLAGE 2 | 33.709 | 82.582 | 66.215 | 31.683 | 41.587
HEEIA | 260.241 | 299.186 | 173.763 | 94.818 | 77.62
HEIGHTS | 35.991 | 72.157 | 48.72 | 23.537 | 19.67
HELEMANO | 540.291 | 153.246 | 84.286 | 47.58 | 59.672
HIGHLANDS | 296.201 | 328.086 | 283.83 | 161.415 | 130.498
HIKINA | 7.149 | 11.686 | 7.589 | 8.632 | 15.437
HILA 1 | 11.683 | 107.832 | 9.816 | 109.897 | 101.928
HILA 2 | 62.56 | 355.634 | 57.762 | 35.353 | 16.935
HILA 3 | 405.41 | 115.483 | 2.29 | 0 | 0
HILA 4 | 0 | 0 | 0 | 0 | 0
HILA 5 | 225.86 | 513.54 | 111.514 | 202.844 | 206.229
HILA 6 | 0 | 0 | 0 | 0 | 0
HOAEAE 1 | 415.689 | 448.542 | 487.854 | 273.472 | 319.79
HOAEAE 2 | 110.242 | 15.207 | 16.57 | 35.612 | 114.181
HOAEAE 3 | 622.517 | 361.479 | 275.39 | 104.706 | 183.407
HOUGHTAILING | 127.255 | 109.967 | 241.174 | 112.034 | 18.579
HUNAKAI | 23.721 | 144.689 | 36.239 | 18.936 | 15.326
ILANIWAI | 100 | 0 | 2.073 | 100 | 100
ILIAINA | 57.537 | 166.102 | 171.237 | 11.097 | 16.191
ILIKAI | 48.958 | 47.243 | 60.769 | 24.733 | 30.546
INDUSTRIAL | 607.38 | 241.563 | 200 | 200 | 100
IWILEI 1 11KV | 202.608 | 208.355 | 205.99 | 100 | 300
IWILEI 13 | 0 | 0 | 0 | 0 | 0
IWILEI 9 | 0 | 0 | 0 | 0 | 0
KAALAKEI | 94.133 | 251.672 | 125.912 | 67.092 | 72.281
KAENA PT | 121.551 | 225.661 | 144.33 | 69.301 | 80.67
KAHAI | 1091.446 | 614.023 | 105.326 | 12.145 | 1.436
KAHALA | 140.18 | 97.087 | 81.479 | 42.254 | 22.75
KAHALA 3 | 4027.09 | 566.668 | 487.187 | 70.299 | 150.588
KAHALA MALL | 77.717 | 312.229 | 60.48 | 73.276 | 43.513
KAHALOA | 39.306 | 61.866 | 56.273 | 36.468 | 29.077
KAHE | 595.322 | 407.41 | 144.222 | 100.001 | 70.943
KAHUKU | 167.381 | 197.916 | 508.957 | 32.813 | 344.14
KAI-HARDING | 11.543 | 24.619 | 2.484 | 18.085 | 7.64
KAI-KAIMUKI | 35.381 | 44.672 | 16.203 | 22.145 | 17.223
KAILUA 1 | 469.069 | 386.832 | 82.129 | 20.627 | 159.111
KAILUA 2 | 789.877 | 1067.67 | 218.158 | 90.506 | 269.573
KAILUA HTS | 169.67 | 209.656 | 161.733 | 190.554 | 108.547
KAINALU | 145.129 | 163.204 | 266.277 | 131.55 | 40.452
KAI-WAIALAE | 35.703 | 53.799 | 43.486 | 17.156 | 25.049
KAI-WILHELMINA | 118.138 | 39.407 | 24.575 | 10.752 | 2.893
KAKAAKO 5 | 13.538 | 11.634 | 12.753 | 15.796 | 7.406
KAKAAKO 6 | 0 | 0 | 0 | 0 | 0
KAKAAKO 8 | 620 | 0 | 306.671 | 400 | 200
KAKAAKO 9 | 233.061 | 102.887 | 24.498 | 0 | 3.841
KALAHEO | 121.984 | 131.504 | 51.293 | 0 | 9.506
KALAHEO 1 | 0 | 100 | 0 | 0 | 0
KALAHEO 2 | 0 | 0 | 0 | 0 | 0
KALAKAUA | 118.151 | 122.041 | 105.835 | 7.78 | 5.835
KALAMA | 13.237 | 129.974 | 126.919 | 18.724 | 122.568
KALIA | 0 | 0 | 0 | 0 | 0
KALIHI | 3.957 | 2.638 | 5.276 | 1.319 | 0
KALIHI KAI | 24.544 | 49.077 | 30.053 | 14.725 | 18.486
KALIHI ST | 43.743 | 47.352 | 52.42 | 41.297 | 27.552
KALIHI UKA | 17.674 | 53.368 | 27.269 | 4.318 | 19.047
KALIHI VALLEY | 40.214 | 34.897 | 68.123 | 22.901 | 32.872
KALOI 1 | 100 | 200 | 100 | 0 | 0
KAM HWY | 97.714 | 159.024 | 56.814 | 57.658 | 135.793
KAM IV | 52.112 | 47.331 | 61.416 | 19.65 | 66.228
KAM TERRACE | 49.23 | 70.544 | 89.327 | 130.369 | 41.567
KAMAKEE | 19.553 | 200 | 2.31 | 3.448 | 4.62
KAMANI | 25.36 | 200 | 100 | 0 | 100
KAMOKILA 1 | 331.495 | 276.285 | 22.56 | 200 | 300
KAMOKILA 2 | 103.796 | 184.554 | 112.449 | 39.817 | 154.547
KAMOKILA 3 | 716 | 400 | 0 | 0 | 100
KAMOKILA 4 | 146.037 | 180.666 | 129.982 | 73.192 | 92.503
KAMOKILA 5 | 0 | 639.987 | 200 | 137.899 | 100
KAMOKILA 6 | 62.903 | 72.488 | 89.139 | 52.387 | 31.366
KAMOKU 10 | 0 | 0 | 0 | 0 | 0
KAMOKU 9 | 0 | 0 | 0 | 0 | 0
KANAINA | 323.592 | 539.862 | 231.644 | 370.845 | 48.636
KANEKAPOLEI | 27.925 | 156.348 | 135.687 | 23.804 | 122.059
KANEOHE 5 | 89.316 | 108.956 | 135.657 | 70.203 | 38.183
KANEOHE 6 | 449.71 | 502.665 | 138.627 | 2.969 | 220.756
KAONOHI 1 | 226.992 | 332.5 | 225.995 | 14.8 | 17.871
KAONOHI 2 | 101.667 | 163.922 | 166.983 | 63.211 | 76.489
KAONOHI 3 | 29.298 | 39.749 | 45.36 | 8.216 | 17.85
KAONOHI 4 | 153.718 | 148.948 | 49.448 | 32.42 | 29.295
KAPAHULU 1 | 108.082 | 10.776 | 16.164 | 4.49 | 6.286
KAPAHULU 2 | 0 | 0 | 0 | 0 | 0
KAPAHULU 3 | 0 | 105.87 | 100 | 0 | 0
KAPAHULU 4 | 8.814 | 19.186 | 18.461 | 38.145 | 5.256
KAPALAMA | 32.798 | 11.623 | 13.705 | 1.803 | 8.729
KAP-HARDING | 42.498 | 51.603 | 44.701 | 29.215 | 26.761
KAPIOLANI 1 | 163.231 | 393.624 | 116.301 | 143.279 | 145.594
KAPIOLANI 2 | 130.277 | 385.811 | 102.061 | 47.801 | 84.182
KAPIOLANI 3 | 275.817 | 496.765 | 86.21 | 36.171 | 56.781
KAP-KAIMUKI | 3.212 | 103.369 | 8.305 | 0 | 1.399
KAPOLEI 1 | 100 | 0 | 0 | 0 | 0
KAPOLEI 2 | 115.523 | 163.683 | 124.292 | 64.505 | 105.809
KAPOLEI 3 | 222.196 | 246.302 | 0 | 100 | 200
KAPOLEI 4 | 5126.352 | 179.243 | 66.655 | 27.164 | 45.581
KAP-WAIALAE | 12.991 | 127.531 | 16.187 | 8.245 | 7.606
KAUHALE | 359.174 | 134.415 | 15.799 | 42.898 | 3.542
KAWAILOA | 90.513 | 96.73 | 95.301 | 38.548 | 27.508
KAWELA | 234.052 | 375.51 | 170.107 | 20.891 | 122.285
KEALAOLU | 5.435 | 14.81 | 32.397 | 10.445 | 12.549
KEAWE | 113.48 | 115.386 | 208.869 | 102.009 | 7.105
KEEHI 1 | 9.66 | 0 | 39.225 | 0 | 100
KEEHI 5 | 0 | 194.456 | 0 | 0 | 0
KEEHI 6 | 4.8 | 100 | 0 | 5.475 | 100
KEEHI 7 | 463 | 200 | 0 | 0 | 0
KEEHI 8 | 300 | 200 | 200 | 100 | 100
KEOLU DR | 335.003 | 134.667 | 130.137 | 74.886 | 265.11
KEWALO | 117.251 | 174.045 | 165.841 | 4735.634 | 83.855
KEWALO 1 | 18.536 | 7.757 | 141.754 | 19.867 | 8.381
KEWALO 2 | 11.869 | 120.804 | 27.17 | 3.937 | 11.212
KEWALO 3 | 0 | 0 | 0 | 0 | 0
KEWALO 4 | 21.187 | 15.273 | 124.303 | 7.543 | 9.247
KEWALO 5 | 0 | 0 | 0 | 0 | 0
KEWALO 6 | 0 | 0 | 0 | 0 | 0
KEWALO 7 | 0 | 0 | 0 | 0 | 0
KILAUEA 12KV | 171.176 | 80.506 | 75.308 | 40.18 | 33.633
KILAUEA 4KV | 25.181 | 57.404 | 31.726 | 19.062 | 8.965
KIPAPA | 378.223 | 19.258 | 32.831 | 118.73 | 212.566
KO OLINA 1 | 140.248 | 134.868 | 32.439 | 11.931 | 16.958
KO OLINA 2 | 0 | 0 | 0 | 0 | 0
KO OLINA 3 | 100 | 100 | 0 | 0 | 0
KOKOHEAD | 87.842 | 105.2 | 99.556 | 59.499 | 49.058
KOLOA | 236.198 | 56.009 | 60.165 | 17.29 | 19.775
KONA ST | 0 | 0 | 0 | 0 | 0
KUAHELANI 1 | 116.788 | 158.222 | 239.128 | 57.532 | 62.022
KUAHELANI 2 | 46.765 | 167.907 | 48.907 | 33.456 | 43.159
KUAHELANI 3 | 114.717 | 161.308 | 143.571 | 157.513 | 88.424
KUAHELANI 4 | 183.652 | 253.591 | 231.621 | 107.709 | 106.084
KUAKINI | 2.114 | 10.678 | 14.017 | 7.119 | 2.323
KUAPA 1 | 109.562 | 142.902 | 139.673 | 67.203 | 58.792
KUAPA 2 | 176.75 | 208.293 | 73.631 | 259.687 | 44.851
KUAPA 3 | 87.186 | 126.022 | 128.343 | 48.017 | 57.321
KUAPA 4 | 187.966 | 314.495 | 116.455 | 51.35 | 155.781
KUHIO | 7.401 | 111.772 | 7.4 | 1.984 | 1.104
KUHIO 1 | 7.299 | 14.735 | 8.342 | 5.16 | 4.432
KUHIO 2 | 100 | 300 | 0 | 100 | 0
KUHIO 3 | 0 | 102.44 | 0 | 0 | 0
KUHIO 4 | 32.265 | 137.669 | 44.634 | 30.157 | 12.684
KUILIMA 1 | 61.734 | 106.463 | 133.008 | 39.324 | 79.697
KUNIA | 12.036 | 107.8 | 5.91 | 6.078 | 10.416
KUNIA MAKAI 1 | 85.356 | 199.612 | 88.923 | 50.799 | 32.762
KUNIA MAKAI 2 | 231.375 | 459.524 | 372.805 | 441.521 | 368.281
KUNIA MAKAI 3 | 74.192 | 172.994 | 120.469 | 244.055 | 51.093
KUNIA MAKAI 4 | 40.453 | 82.029 | 58.71 | 34.423 | 26.99
LAGOON | 4.043 | 500 | 100 | 0 | 4.043
LAKESIDE 1 | 255.844 | 280.448 | 86.972 | 237.436 | 129.223
LAKESIDE 2 | 59.941 | 75.246 | 153.962 | 34.907 | 33.845
LAKESIDE 3 | 193.949 | 106.14 | 195.557 | 249.856 | 87.262
LAKESIDE 4 | 70.147 | 99.588 | 133.24 | 23.571 | 36.848
LANIKAI | 2.409 | 3.879 | 0 | 1.47 | 0
LAULIMA | 88.592 | 100.959 | 93.574 | 40.153 | 66.935
LEAHI | 82.912 | 460.326 | 327.296 | 83.074 | 162.628
LEOMELE | 138.514 | 144.294 | 158.917 | 77.446 | 64.575
LEOOLE | 310.321 | 412.986 | 250.701 | 200 | 22.16
LIBERTY HOUSE | 0 | 0 | 0 | 0 | 0
LIGHTHOUSE | 300 | 101.813 | 0 | 0 | 100
LIKELIKE | 21.014 | 37.274 | 30.642 | 18.575 | 21.007
LILIHA MAKAI | 1.973 | 4.272 | 13.141 | 3.613 | 3.66
LOWREY | 44.453 | 78.868 | 47.046 | 38.807 | 32.939
LUAWAI | 624.305 | 151.187 | 135.882 | 72.547 | 66.155
LUMIAUAU | 109.29 | 112.133 | 174.161 | 133.709 | 50.492
MACHADO ST | 23.881 | 31.686 | 27.609 | 19.234 | 44.817
MAHUKONA | 109.361 | 110.468 | 8.002 | 2.753 | 7.592
MAKAHA | 525.577 | 406.698 | 193.315 | 283.096 | 113.29
MAKAHA VALLEY | 45.236 | 42.345 | 26.243 | 12.54 | 25.731
MAKAKILO 1 | 222.558 | 378.598 | 361.595 | 97.096 | 170.952
MAKAKILO 2 | 368.413 | 3354.075 | 612.574 | 112.555 | 207.897
MAKAKILO 3 | 142.228 | 167.569 | 174.012 | 83.795 | 73.786
MAKAKILO 4 | 42.488 | 51.431 | 36.932 | 39.526 | 19.375
MAKALAPA-MOANALUA | 107.203 | 442.598 | 234.568 | 151.03 | 171.158
MAKALOA | 116.662 | 29.808 | 122.561 | 103.905 | 10.298
MALAKOLE | 0 | 0 | 0 | 0 | 0
MALAKOLE 4 | 504.59 | 2541.02 | 0 | 0 | 100
MANAGERS | 38.74 | 82.827 | 92.637 | 22.315 | 34.645
MANOA 1 | 53.786 | 86.025 | 127.435 | 51.809 | 47.369
MANOA 2 | 47.308 | 112.068 | 49.522 | 30.049 | 47.288
MANOA 3 | 138.149 | 270.984 | 107.911 | 20.58 | 26.436
MANOA 4 | 0 | 0 | 0 | 0 | 0
MANOA-MCCULLY | 10.956 | 151.143 | 122.536 | 7.252 | 4.099
MANOA-PIIKOI | 184.315 | 333.134 | 91.939 | 258.298 | 41.208
MAPUNAPUNA | 208.973 | 113.43 | 0 | 100 | 100
MAPUNAPUNA-MOANALUA | 139.071 | 137.543 | 249.126 | 117.068 | 16.676
MAUKA | 588.515 | 1724.234 | 731.337 | 315.809 | 619.51
MAUNALANI | 41.665 | 84.04 | 61.002 | 127.73 | 85.744
MAUNAWILI | 0 | 0 | 0 | 0 | 0
MCCULLY 1 | 42.276 | 214.17 | 64.009 | 150.448 | 40.535
MCCULLY 3 | 302.054 | 415.16 | 306.162 | 322.067 | 101.027
MCCULLY 5 | 94.373 | 71.115 | 93.558 | 39.251 | 24.349
MIKILUA 1 | 111.369 | 197.221 | 101.446 | 187.1 | 47.166
MIKILUA 3 | 416.022 | 334.338 | 167.398 | 372.84 | 84.152
MIKILUA 4 | 179.673 | 614.747 | 196.442 | 165.173 | 71.836
MIKILUA 5 | 403.41 | 356.022 | 334.641 | 196.596 | 201.711
MILILANI 1 | 128.396 | 242.525 | 102.007 | 60.465 | 64.625
MILILANI 2 | 101.731 | 146.984 | 114.456 | 53.606 | 58.939
MILILANI 3 | 76.565 | 52.069 | 67.922 | 117.995 | 123.909
MILILANI 4 | 274.064 | 181.366 | 145.928 | 177.337 | 121.614
MOILIILI 1 | 378.016 | 190.573 | 75.577 | 35.434 | 37.663
MOILIILI 2 | 96.045 | 124.93 | 109.045 | 60.133 | 46.824
MOKAUEA | 8.73 | 66.564 | 15.701 | 11.158 | 8.644
MOKUOLA | 663.116 | 260.966 | 188.762 | 255.584 | 137.813
MOKUONE 1 | 0 | 0 | 0 | 0 | 0
MOKUONE 2 | 0 | 300 | 100 | 6.45 | 100
NIU | 205.972 | 532.986 | 126.715 | 61.996 | 78.636
NUMANA | 11.294 | 40.829 | 14.024 | 16.007 | 19.548
NUUANU | 135.452 | 45.155 | 50.67 | 117.689 | 15.235
NUUANU 2 | 245.094 | 324.696 | 240.607 | 23.919 | 26.79
NUUANU 3 | 274.053 | 391.789 | 199.135 | 62.976 | 49.014
OCEAN POINTE 1 | 238.936 | 519.339 | 218.381 | 86.926 | 103.109
OCEAN POINTE 2 | 192.363 | 324.357 | 227.908 | 121.554 | 136.337
OCEAN POINTE 3 | 184.957 | 268.398 | 210.118 | 99.144 | 97.531
OCEAN POINTE 4 | 50.385 | 84.996 | 89.94 | 49.208 | 32.099
OLOMANA | 925.751 | 177.353 | 24.894 | 21.445 | 6.428
ONEAWA | 24.829 | 36.856 | 33.834 | 15.378 | 20.154
PAHIA | 479.412 | 250.015 | 195.814 | 47.149 | 44.952
PAIWA | 206.929 | 109.689 | 119.288 | 52.756 | 45.666
PALEKA | 105.238 | 173.659 | 74.43 | 48.777 | 123.072
PALI | 224.645 | 138.641 | 107.885 | 78.669 | 36.119
PAOAKALANI | 210.081 | 714.693 | 17.986 | 205.072 | 5.853
PAUOA 1 | 58.307 | 90.705 | 81.731 | 90.183 | 52.811
PAUOA 2 | 332.121 | 285.384 | 258.771 | 140.321 | 124.343
PAWAA KAI | 111.466 | 316.761 | 24.009 | 8.247 | 2.686
PAWAINA | 38.179 | 64.434 | 87.99 | 53.852 | 21.685
PEARL CITY 1 | 185.637 | 325.828 | 474.357 | 106.526 | 12.912
PEARL CITY 2 | 230.45 | 171.114 | 165.347 | 65.756 | 144.085
PENINSULA | 137.119 | 571.215 | 82.771 | 33.514 | 358.253
PENSACOLA | 122.489 | 439.459 | 268.199 | 42.601 | 417.523
PIIKOI | 195.295 | 105.406 | 88.247 | 45.749 | 51.382
PIIKOI 7 | 200.656 | 141.287 | 15.186 | 203.41 | 5.891
PIIKOI 8 | 213.921 | 280.874 | 219.78 | 55.887 | 139.612
POAMOHO | 0 | 0 | 0 | 0 | 0
POHAKUPU 4 | 97.185 | 232.125 | 281.898 | 171.836 | 93.435
PORTLOCK | 372.466 | 490.417 | 757.284 | 113.329 | 125.768
PUNALUU | 194.058 | 190.051 | 181.161 | 275.928 | 73.426
PUNCHBOWL | 36.293 | 36.013 | 48.568 | 19.588 | 12.684
PUOHALA 1 | 60.127 | 89.435 | 63.303 | 25.425 | 69.614
PUOHALA 2 | 269.31 | 238.512 | 227.498 | 115.78 | 120.395
PUUHALE | 13.971 | 18.537 | 130.874 | 122.494 | 127.068
PUUNUI | 32.141 | 73.39 | 38.862 | 29.726 | 30.08
QUEEN ST | 300 | 4.558 | 0 | 0 | 0
QUEENS 1 | 85.637 | 103.45 | 92.102 | 84.577 | 59.051
QUEENS 2 | 146.776 | 42.918 | 152.021 | 30.27 | 9.575
RUGER | 26.416 | 13.02 | 21.318 | 12.604 | 9.649
SAND ISLAND | 107.157 | 21.01 | 2.486 | 4.447 | 1.412
SAND ISLAND 1 | 0 | 0 | 0 | 0 | 0
SAND ISLAND 2 | 363 | 100 | 0 | 0 | 0
SCHOOL ST | 98.622 | 236.668 | 126.255 | 44.648 | 151.782
SCHOOL ST 3 | 249.71 | 270.461 | 163.614 | 119.74 | 129.354
SHAFTER | 100 | 0 | 0 | 100 | 0
SHERATON 1 | 16.612 | 26.925 | 15.629 | 12.161 | 5.259
SHERATON 2 | 10.032 | 1.646 | 3.473 | 10.032 | 8.205
SHOPPING CTR | 0 | 27.732 | 19.879 | 0 | 19.879
SOUTH RAMP 1 | 825 | 600 | 100 | 300 | 100
ST LOUIS | 165.984 | 297.477 | 84.518 | 42.661 | 136.6
ST LOUIS HTS | 14.683 | 5.137 | 5.736 | 4.889 | 0
THURSTON | 85.938 | 326.758 | 124.129 | 41.985 | 49.622
TOWN | 0 | 1.622 | 0 | 0 | 0.811
UALENA | 29.89 | 23.283 | 6.87 | 0 | 0
UPLANDS | 132.295 | 40.827 | 31.548 | 17.282 | 26.807
UWAPO 1 | 153.212 | 181.552 | 187.438 | 104.84 | 74.879
UWAPO 2 | 44.46 | 76.689 | 55.136 | 17.716 | 21.465
UWAPO 3 | 148.562 | 165.466 | 178.978 | 78.503 | 105.253
UWAPO 4 | 0 | 3.353 | 2.987 | 0 | 0
WAHIAWA HTS | 275.389 | 436.719 | 342.559 | 214.176 | 107.619
WAHIAWA PROPER | 42.875 | 51.888 | 77.313 | 26.875 | 24.13
WAIAKAMILO 1 | 3.665 | 20.294 | 20.185 | 22.95 | 3.665
WAIAKAMILO 2 | 213.106 | 221.947 | 104.319 | 1.954 | 5.126
WAIAKAMILO 3 | 142.982 | 253.34 | 155.016 | 35.74 | 19.857
WAIAKAMILO 4 | 152.324 | 237.947 | 125.32 | 11.699 | 114.297
WAIAKAMILO-IWILEI | 31.825 | 41.081 | 34.739 | 10.144 | 115.572
WAIAKAMILO-KAPALAMA | 219.898 | 548.106 | 100 | 7.32 | 0
WAIALAE NUI | 48.881 | 154.197 | 45.211 | 130.214 | 332.021
WAIALAE SC | 0 | 0 | 0 | 0 | 0
WAIALUA | 386.388 | 230.323 | 280.611 | 151.401 | 55.103
WAIAWA 1 | 1021.41 | 510.064 | 104.528 | 60.371 | 164.819
WAIAWA 2 | 1047.032 | 316.517 | 22.221 | 0 | 12.45
WAIAWA 3 | 45.125 | 160.014 | 44.911 | 22.427 | 25.887
WAIAWA 4 | 70.794 | 243.82 | 126.536 | 158.356 | 61.458
WAIHEE 1 | 99.017 | 303.494 | 133.054 | 163.549 | 259.479
WAIHEE 2 | 119.824 | 198.74 | 133.697 | 75.179 | 48.366
WAIHEE 3 | 11.22 | 143.353 | 73.236 | 71.451 | 14.955
WAIHEE 4 | 285.012 | 233.48 | 359.81 | 104.761 | 108.574
WAIKELE CTR | 100 | 0 | 0 | 0 | 0
WAIKIKI 1 | 105.623 | 125.268 | 14.923 | 8.058 | 7.455
WAIKIKI 2 | 100 | 0 | 0 | 100 | 0
WAIKIKI 3 | 103.146 | 25.481 | 16.874 | 0 | 3.146
WAIKIKI 4 | 132.583 | 8.294 | 5.446 | 5.184 | 6.769
WAIKIKI 5 | 131.852 | 333.933 | 41.323 | 26.26 | 14.148
WAIKIKI 6 | 0 | 227.704 | 27.704 | 100 | 200
WAILANI | 67.744 | 97.467 | 65.04 | 31.591 | 50.714
WAILUPE | 500.032 | 445.226 | 668.903 | 280.424 | 223.675
WAIMALU 1 | 1929.697 | 186.152 | 65.198 | 25.891 | 61.844
WAIMALU 2 | 142.9 | 253.504 | 179.545 | 90.501 | 182.132
WAIMALU 3 | 287.442 | 331.169 | 282.901 | 152.237 | 139.98
WAIMALU 4 | 154.069 | 176.057 | 181.352 | 20.251 | 73.817
WAIMANALO | 177.851 | 269.044 | 199.801 | 153.986 | 54.017
WAIMANO 5 | 87.844 | 81.842 | 103.354 | 48.807 | 75.506
WAIMANO 6 | 89.115 | 211.505 | 290.111 | 60.657 | 73.61
WAIMANO HOME RD | 218.399 | 324.281 | 275.668 | 126.764 | 132.446
WAIMEA 1 | 44.109 | 36.694 | 117.216 | 10.791 | 11.892
WAIMEA 2 | 96.006 | 377.658 | 168.273 | 53.639 | 72.947
WAIOMAO | 328.676 | 302.981 | 269.409 | 162.031 | 190.147
WAIPAHU | 550.451 | 894.524 | 621.038 | 315.49 | 384.835
WAIPIO 1 | 233.178 | 233.476 | 140.44 | 18.577 | 214.299
WAIPIO 2 | 150.676 | 45.24 | 132.051 | 223.942 | 22.182
WAIWAI | 0 | 100 | 0 | 0 | 0
WAI-WILHELMINA | 31.482 | 72.282 | 51.514 | 20.565 | 13.416
WHITMORE | 11.171 | 3.448 | 6.464 | 6.452 | 1.633
WILIWILI | 53.543 | 131.935 | 87.852 | 55.794 | 72.681
WILIWILI 2 | 46.535 | 69.536 | 76.156 | 35.993 | 42.991
WOODLAWN | 25.231 | 58.953 | 51.398 | 13.102 | 25.384

## Hawaii Island Circuit DER Growt
Return to Assumptions Summary
Hawai‘i Island Adjusted DER Growth by Circuit - Base Forecast
The Adjusted DER Growth by Circuit shows the annual DER growth by circuit. The forecast is shown by circuit (or feeder) peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth (kW)
Circuit | 2021 | 2022 | 2023 | 2024 | 2025
Ainaloa 11 | 59.2435 | 46.453 | 50.009 | 33.7644 | 36.752
Ainaloa 12 | 41.6869 | 32.6868 | 35.189 | 23.7584 | 25.8607
Anaehoomalu 11 | 14.9073 | 11.6889 | 12.5836 | 8.4961 | 9.2478
Anaehoomalu 12 | 25.4081 | 19.9226 | 21.4476 | 14.4807 | 15.762
Anaehoomalu 13 | 18.099 | 14.1915 | 15.2778 | 10.3151 | 11.2278
Captain Cook 11 | 124.814 | 97.8671 | 105.3587 | 71.1347 | 77.429
Captain Cook 12 | 95.3821 | 74.7894 | 80.5145 | 54.3607 | 59.1708
Hakalau 1 | 13.7424 | 10.7754 | 11.6003 | 7.8321 | 8.5251
Halaula 1 | 49.9136 | 39.1374 | 42.1333 | 28.447 | 30.9641
Halaula 2 | 0 | 0 | 0 | 0 | 0
Hale Pohaku 11 | 19.8323 | 15.5506 | 16.741 | 11.303 | 12.3031
Hale Pohaku 12 | 8.3662 | 6.5599 | 7.0621 | 4.7681 | 5.19
Haleaha 11 | 40.3279 | 31.6212 | 34.0418 | 22.9839 | 25.0176
Haleaha 12 | 125.0746 | 98.0714 | 105.5787 | 71.2832 | 77.5907
Hawaiian Beaches 11 | 63.6284 | 49.8912 | 53.7103 | 36.2634 | 39.4722
Hawaiian Beaches 12 | 0.46905 | 0.36778 | 0.39594 | 0.26732 | 0.29098
Hawaiian Paradise Park 11 | 59.73 | 46.8345 | 50.4197 | 34.0417 | 37.0539
Hawaiian Paradise Park 12 | 115.8527 | 90.8405 | 97.7943 | 66.0274 | 71.8699
Hawaiian Paradise Park 13 | 305.3547 | 239.4296 | 257.7578 | 174.0294 | 189.4284
Hawaiian Paradise Park 14 | 51.8783 | 40.678 | 43.7918 | 29.5668 | 32.183
Hawi 11 | 40.77 | 31.9679 | 34.415 | 23.2359 | 25.2919
Hawi 12 | 31.6497 | 24.8166 | 26.7163 | 18.038 | 19.6341
Honokaa 12 | 47.3641 | 37.1384 | 39.9813 | 26.994 | 29.3826
Honokaa 14 | 63.395 | 49.7083 | 53.5134 | 36.1304 | 39.3275
Honomu 1 | 18.5385 | 14.5361 | 15.6489 | 10.5656 | 11.5005
Host Park 11 | 80.4577 | 63.0871 | 67.9164 | 45.8549 | 49.9124
Host Park 12 | 0 | 0 | 0 | 0 | 0
Host Park 13 | 6.7808 | 5.3168 | 5.7238 | 3.8645 | 4.2065
Host Park 14 | 42.641 | 33.435 | 35.9944 | 24.3022 | 26.4526
Huehue 11 | 468.7964 | 367.5848 | 395.7231 | 267.1789 | 290.8204
Kahaluu 11 | 156.7459 | 122.905 | 132.3133 | 89.3335 | 97.2382
Kahaluu 12 | 88.4918 | 69.3867 | 74.6982 | 50.4337 | 54.8963
Kahaluu 14 | 21.9537 | 17.2139 | 18.5316 | 12.5119 | 13.6191
Kahaluu 15 | 142.9424 | 112.0816 | 120.6614 | 81.4665 | 88.6751
Kailua 11 | 187.4698 | 146.9957 | 158.2481 | 106.8438 | 116.2979
Kailua 12 | 2.6437 | 2.073 | 2.2317 | 1.5067 | 1.6401
Kailua 15 | 250.9663 | 196.7835 | 211.8471 | 143.032 | 155.6883
Kaloko 11 | 128.1201 | 100.4594 | 108.1495 | 73.0189 | 79.48
Kaloko 12 | 24.7338 | 19.3938 | 20.8784 | 14.0964 | 15.3437
Kaloko 13 | 83.6771 | 65.6115 | 70.634 | 47.6897 | 51.9095
Kaloko 14 | 3.6003 | 2.823 | 3.0391 | 2.0519 | 2.2334
Kamuela 11 | 2.9388 | 2.3043 | 2.4807 | 1.6749 | 1.8231
Kamuela 12 | 95.0141 | 74.5009 | 80.2039 | 54.151 | 58.9425
Kanoelehua 11 | 57.2044 | 44.8542 | 48.2877 | 32.6022 | 35.4871
Kanoelehua 1101 | 61.6005 | 48.3012 | 51.9986 | 35.1077 | 38.2142
Kanoelehua 12 | 48.155 | 37.7585 | 40.6488 | 27.4447 | 29.8732
Kanoelehua 13 | 8.1018 | 6.3526 | 6.8389 | 4.6174 | 5.026
Kanoelehua 14 | 92.1841 | 72.2818 | 77.8149 | 52.538 | 57.1869
Kanoelehua 1401 | 85.3358 | 66.9121 | 72.0342 | 48.635 | 52.9385
Kanoelehua 15 | 108.8472 | 85.3475 | 91.8807 | 62.0348 | 67.524
Kanoelehua 17 | 36.4641 | 28.5916 | 30.7803 | 20.7818 | 22.6207
Kapua 11 | 21.0038 | 16.4691 | 17.7298 | 11.9706 | 13.0298
Kapua 12 | 56.3286 | 44.1675 | 47.5485 | 32.1031 | 34.9438
Kauhale 11 | 72.1107 | 56.5422 | 60.8705 | 41.0977 | 44.7343
Kauhale 12 | 12.4755 | 9.7821 | 10.5309 | 7.1101 | 7.7392
Kaumana 11 | 183.7113 | 144.0486 | 155.0754 | 104.7017 | 113.9663
Kaumana 12 | 53.1461 | 41.672 | 44.862 | 30.2893 | 32.9695
Kawaihae 11 | 17.0654 | 13.381 | 14.4053 | 9.726 | 10.5866
Kawaihae 12 | 29.8871 | 23.4346 | 25.2285 | 17.0334 | 18.5406
Kawaihae 13 | 1.4498 | 1.1368 | 1.2238 | 0.82628 | 0.89939
Kawailani 11 | 158.0808 | 123.9516 | 133.44 | 90.0942 | 98.0662
Kawailani 12 | 151.0464 | 118.436 | 127.5022 | 86.0852 | 93.7025
Keahole Airport 11 | 84.6084 | 66.3417 | 71.4201 | 48.2204 | 52.4873
Keahole Airport 12 | 23.5856 | 18.4936 | 19.9092 | 13.442 | 14.6315
Keahole Airport 13 | 53.7713 | 42.1623 | 45.3897 | 30.6456 | 33.3573
Keahuolu 11 | 16.3802 | 12.8438 | 13.827 | 9.3355 | 10.1616
Keahuolu 12 | 43.7203 | 34.2812 | 36.9054 | 24.9173 | 27.1221
Kealakehe 11 | 50.9927 | 39.9836 | 43.0443 | 29.062 | 31.6336
Kealia 11 | 22.6253 | 17.7406 | 19.0986 | 12.8948 | 14.0358
Kealia 12 | 37.93 | 29.741 | 32.0177 | 21.6173 | 23.5301
Keauhou 11 | 83.2063 | 65.2424 | 70.2366 | 47.4214 | 51.6175
Keauhou 13 | 92.5593 | 72.5761 | 78.1317 | 52.7519 | 57.4197
Komohana 12 | 246.4837 | 193.2687 | 208.0632 | 140.4773 | 152.9075
Komohana 13 | 224.1021 | 175.7192 | 189.1703 | 127.7214 | 139.0229
Komohana 14 | 17.2168 | 13.4998 | 14.5332 | 9.8123 | 10.6806
Kuakini 11 | 296.3032 | 232.3323 | 250.1171 | 168.8707 | 183.8133
Kuakini 13 | 70.458 | 55.2464 | 59.4754 | 40.1558 | 43.709
Kuakini 14 | 292.863 | 229.6349 | 247.2132 | 166.9101 | 181.6792
Kulani 12 | 2.422 | 1.8991 | 2.0445 | 1.3804 | 1.5025
Kurtistown 12 | 71.1146 | 55.7612 | 60.0297 | 40.53 | 44.1163
Lalamilo 11 | 55.2615 | 43.3307 | 46.6477 | 31.4949 | 34.2818
Lalamilo 12 | 20.4372 | 16.0249 | 17.2515 | 11.6477 | 12.6783
Laupahoehoe 1 | 6.7535 | 5.2954 | 5.7008 | 3.849 | 4.1896
Laupahoehoe 2 | 14.2963 | 11.2097 | 12.0678 | 8.1478 | 8.8688
Maliu Ridge 11 | 26.059 | 20.4329 | 21.997 | 14.8517 | 16.1658
Maliu Ridge 12 | 32.5238 | 25.502 | 27.4542 | 18.5361 | 20.1763
Mauna Lani 11 | 185.1605 | 145.185 | 156.2988 | 105.5277 | 114.8653
Mauna Lani 13 | 64.53 | 50.5982 | 54.4714 | 36.7773 | 40.0315
Mauna Lani 14 | 281.4309 | 220.6709 | 237.563 | 160.3946 | 174.5872
Mountain View 11 | 75.2193 | 58.9797 | 63.4946 | 42.8694 | 46.6627
Mountain View 12 | 14.4006 | 11.2915 | 12.1559 | 8.2072 | 8.9335
Namakani Paio | 14.2992 | 11.2121 | 12.0704 | 8.1495 | 8.8706
Ookala | 12.7706 | 10.0134 | 10.78 | 7.2783 | 7.9223
Orchid Isle 11 | 4.6044 | 3.6103 | 3.8867 | 2.6242 | 2.8564
Orchid Isle 12 | 26.1104 | 20.4732 | 22.0405 | 14.881 | 16.1977
Ouli 11 | 39.9681 | 31.3391 | 33.7381 | 22.7789 | 24.7944
Ouli 12 | 75.1635 | 58.936 | 63.4475 | 42.8376 | 46.6281
Paauilo 1 | 18.5871 | 14.5742 | 15.6899 | 10.5933 | 11.5306
Pahala 11 | 26.6848 | 20.9236 | 22.5253 | 15.2083 | 16.554
Pahala 12 | 5.3267 | 4.1767 | 4.4964 | 3.0358 | 3.3045
Palani 11 | 7.2706 | 5.7009 | 6.1373 | 4.1437 | 4.5103
Palani 12 | 154.3069 | 120.9926 | 130.2545 | 87.9434 | 95.7251
Palani 13 | 0 | 0 | 0 | 0 | 0
Palani 14 | 52.619 | 41.2588 | 44.4171 | 29.9889 | 32.6425
Panaewa 11 | 83.1555 | 65.2025 | 70.1937 | 47.3924 | 51.586
Panaewa 12 | 147.5474 | 115.6924 | 124.5485 | 84.091 | 91.5318
Papaaloa 1 | 12.7211 | 9.9747 | 10.7382 | 7.2501 | 7.8916
Papaaloa 2 | 8.3026 | 6.5101 | 7.0085 | 4.7319 | 5.1506
Poopoomino 11 | 117.7264 | 92.3096 | 99.3759 | 67.0952 | 73.0322
Poopoomino 12 | 60.2381 | 47.2329 | 50.8485 | 34.3312 | 37.369
Poopoomino 13 | 46.2996 | 36.3037 | 39.0827 | 26.3873 | 28.7222
Poopoomino 14 | 112.6031 | 88.2924 | 95.0511 | 64.1753 | 69.8539
Punaluu 11 | 1.0916 | 0.85594 | 0.92146 | 0.62214 | 0.67719
Punaluu 12 | 12.0486 | 9.4473 | 10.1705 | 6.8668 | 7.4744
Puueo 11 | 96.244 | 75.4652 | 81.242 | 54.8519 | 59.7055
Puueo 12 | 98.8916 | 77.5412 | 83.4769 | 56.3608 | 61.3479
Puueo 1402 | 70.7087 | 55.4429 | 59.687 | 40.2987 | 43.8645
Puuhuluhulu 11 | 45.4809 | 35.6618 | 38.3916 | 25.9207 | 28.2143
Puuhuluhulu 12 | 45.4809 | 35.6618 | 38.3916 | 25.9207 | 28.2143
Puukapu 11 | 94.7839 | 74.3204 | 80.0095 | 54.0197 | 58.7997
Puuwaawaa 11 | 100 | 0 | 0 | 0 | 0
Puuwaawaa 12 | 18.436 | 14.4557 | 15.5623 | 10.5072 | 11.4369
Royal Hawaiian | 20.5717 | 16.1303 | 17.3651 | 11.7243 | 12.7617
Shipman 11 | 25.8149 | 20.2415 | 21.791 | 14.7126 | 16.0144
Shipman 12 | 93.9724 | 73.6841 | 79.3245 | 53.5573 | 58.2963
South Point 11 | 801.9245 | 40.7142 | 43.8308 | 29.5931 | 32.2117
South Point 12 | 3.6066 | 2.8279 | 3.0444 | 2.0555 | 2.2374
Umauma 11 | 5.1221 | 4.0163 | 4.3237 | 2.9192 | 3.1775
Umauma 12 | 8.8557 | 6.9438 | 7.4753 | 5.0471 | 5.4937
Waika 11 | 7.6223 | 5.9766 | 6.4341 | 4.3441 | 4.7285
Waika 12 | 135.9772 | 106.6202 | 114.7818 | 77.4968 | 84.3542
Waikii 11 | 28.8253 | 22.6021 | 24.3322 | 16.4283 | 17.882
Waikii 12 | 13.5978 | 10.6621 | 11.4783 | 7.7497 | 8.4355
Waikoloa 11 | 119.959 | 94.0602 | 101.2605 | 68.3677 | 74.4172
Waikoloa 12 | 300.8217 | 235.8753 | 253.9314 | 171.4459 | 186.6164
Waipunahina 11 | 22.5817 | 17.7064 | 19.0618 | 12.8699 | 14.0087
Wright Road 11 | 64.2827 | 50.4043 | 54.2627 | 36.6364 | 39.8781

## Maui Circuit DER Growth
Return to Assumptions Summary
Maui Island Adjusted DER Growth by Circuit - Base Forecast
The Adjusted DER Growth by Circuit shows the annual DER growth by circuit. The forecast is shown by circuit (or feeder) peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth (kW)
Circuit | 2021 | 2022 | 2023 | 2024 | 2025
Haiku 16/1358 | 182.6631 | 166.113 | 160.0708 | 109.2506 | 110.3701
Haiku 16/1361 | 53.0253 | 48.221 | 46.467 | 31.7144 | 32.0394
Hana 41/10277 | 6.3999 | 5.82 | 5.6083 | 3.8277 | 3.867
Hana 41/537 | 10.304 | 9.3704 | 9.0296 | 6.1628 | 6.226
Hana 41/6528 | 3.2267 | 2.9343 | 2.8276 | 1.9299 | 1.9497
Huelo 74A/Huelo | 13.2689 | 12.0666 | 11.6277 | 7.9361 | 8.0174
Kahului 8/1264 | 72.7008 | 66.1138 | 63.709 | 43.4823 | 43.9279
Kahului 8/1265 | 211.4063 | 192.2519 | 185.259 | 126.4419 | 127.7375
Kahului 8/4048 | 94.6409 | 86.066 | 82.9354 | 56.6046 | 57.1846
Kahului 8/4049 | 80.4342 | 73.1465 | 70.4859 | 48.1076 | 48.6006
Kahului 8/4050 | 34.8823 | 31.7218 | 30.568 | 20.8631 | 21.0769
Kailua 9/Kailua | 1.1106 | 1.01 | 0.97324 | 0.66425 | 0.67106
Kanaha 2/1244 | 131.5946 | 119.6715 | 115.3186 | 78.7066 | 79.5131
Kanaha 2/1245 | 89.083 | 81.0117 | 78.065 | 53.2804 | 53.8264
Kanaha 2/1304 | 140.9563 | 128.185 | 123.5225 | 84.3058 | 85.1697
Kanaha 2/1305 | 171.0692 | 155.5696 | 149.9109 | 102.3163 | 103.3647
Kanaha 2/1347 | 158.9051 | 144.5076 | 139.2513 | 95.041 | 96.0149
Kanaha 2/1348 | 49.8356 | 45.3203 | 43.6718 | 29.8066 | 30.112
Kaonoulu/1590 | 326.6184 | 297.0252 | 286.2213 | 195.3501 | 197.3518
Kaonoulu/1591 | 88.3684 | 80.3618 | 77.4388 | 52.8531 | 53.3946
Kauhikoa 98/1295 | 69.1699 | 62.9028 | 60.6148 | 41.3704 | 41.7943
Keanae 42/Keanae | 2.4207 | 2.2014 | 2.1213 | 1.4478 | 1.4627
Kihei 35/1253 | 127.6912 | 116.1218 | 111.898 | 76.372 | 77.1545
Kihei 35/1254 | 281.5763 | 256.0642 | 246.7502 | 168.4105 | 170.1362
Kihei 35/1384 | 370.9155 | 337.3088 | 325.0396 | 221.8441 | 224.1174
Kihei 35/1385 | 106.8768 | 97.1933 | 93.658 | 63.9229 | 64.5779
Kihei 35/1473 | 263.2907 | 239.4353 | 230.7262 | 157.4739 | 159.0875
Kihei 35/1515 | 537.8182 | 489.0894 | 471.2994 | 321.6685 | 324.9646
Kuau 73/4066 | 60.7894 | 55.2816 | 53.2708 | 36.3581 | 36.7306
Kuihelani 209/1653 | 361.8787 | 329.0908 | 317.1205 | 216.4392 | 218.6571
Kuihelani 209/1708 | 172.1638 | 156.5649 | 150.8701 | 102.971 | 104.0261
Kula 13/1237 | 230.8684 | 209.9506 | 202.3139 | 138.0821 | 139.497
Kula 13/1238 | 232.7116 | 211.6268 | 203.9292 | 139.1846 | 140.6108
Kula Ag Park 55/1322 | 42.9009 | 39.0139 | 37.5948 | 25.659 | 25.9219
Lahaina 34/1221 | 169.3264 | 153.9847 | 148.3837 | 101.2739 | 102.3117
Lahaina 34/1223 | 236.945 | 215.4766 | 207.6389 | 141.7165 | 143.1687
Lahaina 34/1225 | 47.7638 | 43.4362 | 41.8563 | 28.5675 | 28.8602
Lahaina 34/1226 | 26.7334 | 24.3112 | 23.4269 | 15.9892 | 16.153
Lahaina 34/1390 | 212.7515 | 193.4752 | 186.4378 | 127.2464 | 128.5503
Lahaina 34/1397 | 16.6961 | 15.1833 | 14.6311 | 9.9859 | 10.0882
Lahaina 34/1398 | 303.5239 | 276.0232 | 265.9833 | 181.5373 | 183.3975
Maalaea 39/1285 | 68.0455 | 61.8803 | 59.6294 | 40.6979 | 41.115
Maalaea 39/1286 | 90.6241 | 82.4132 | 79.4155 | 54.2022 | 54.7576
Mahinahina 50/1219 | 172.5351 | 156.9026 | 151.1955 | 103.1931 | 104.2505
Mahinahina 50/1380 | 40.815 | 37.117 | 35.7669 | 24.4114 | 24.6615
Mahinahina 50/1381 | 1180.5344 | 164.1771 | 158.2054 | 107.9774 | 109.0838
Makawao 12/1234 | 67.0563 | 60.9807 | 58.7626 | 40.1063 | 40.5173
Makawao 12/1235 | 103.2843 | 93.9263 | 90.5098 | 61.7742 | 62.4072
Makawao 12/1236 | 92.0432 | 83.7036 | 80.659 | 55.0509 | 55.615
Maui Hardwoods 75/522 | 16.5121 | 15.016 | 14.4698 | 9.8759 | 9.9771
Napili 29/1232 | 41.8179 | 38.029 | 36.6458 | 25.0113 | 25.2676
Napili 29/1420 | 884.6695 | 122.4678 | 118.0132 | 80.5457 | 81.371
Napili 29/1421 | 78.669 | 71.5412 | 68.939 | 47.0518 | 47.534
Onehee 40/4055 | 103.7759 | 94.3733 | 90.9406 | 62.0682 | 62.7043
Onehee 40/4056 | 42.5612 | 38.705 | 37.2971 | 25.4558 | 25.7166
Paia Mauka 93/4042 | 102.8038 | 93.4893 | 90.0887 | 61.4868 | 62.1169
Peahi 94/1294 | 92.7857 | 84.3789 | 81.3097 | 55.495 | 56.0637
Pukalani 17/1282 | 246.3526 | 224.0319 | 215.883 | 147.3432 | 148.853
Pukalani 17/1283 | 0.54898 | 0.49924 | 0.48108 | 0.32834 | 0.33171
Pukalani 17/1308 | 345.5494 | 314.241 | 302.8109 | 206.6727 | 208.7905
Pukalani 17/1309 | 36.6928 | 33.3683 | 32.1545 | 21.9459 | 22.1708
Puukolii 23/1270 | 448.4704 | 407.8369 | 393.0023 | 268.2296 | 270.9782
Puukolii 23/1271 | 93.0611 | 84.6294 | 81.5511 | 55.6598 | 56.2301
Puukolii 23/1272 | 251.3 | 228.531 | 220.2185 | 150.3022 | 151.8424
Puukolii 23/1273 | 8.6505 | 7.8667 | 7.5805 | 5.1738 | 5.2268
Spreckelsville 92/4043 | 84.2181 | 76.5876 | 73.8018 | 50.3708 | 50.8869
Waiehu 43/1378 | 159.9311 | 145.4405 | 140.1503 | 95.6546 | 96.6347
Waiehu 43/1379 | 295.254 | 268.5026 | 258.7361 | 176.5911 | 178.4006
Waiinu 36/1266 | 88.4897 | 80.4722 | 77.5451 | 52.9256 | 53.4679
Waiinu 36/1267 | 47.4854 | 43.183 | 41.6123 | 28.401 | 28.692
Waiinu 36/1492 | 80.5622 | 73.2629 | 70.598 | 48.1842 | 48.6779
Waiinu 36/1493 | 659.4366 | 599.6886 | 577.8757 | 394.4083 | 398.4498
Waiinu 36/2030 | 25.3655 | 23.0673 | 22.2282 | 15.1711 | 15.3265
Waikapu 77/524 | 0 | 0 | 0 | 0 | 0
Wailea 25/1280 | 225.35 | 204.9322 | 197.4781 | 134.7816 | 136.1627
Wailea 25/1281 | 55.4806 | 50.4538 | 48.6186 | 33.1829 | 33.5229
Wailea 25/1320 | 196.6657 | 178.8469 | 172.3415 | 117.6255 | 118.8308
Wailea 25/1321 | 2.521 | 2.2926 | 2.2092 | 1.5078 | 1.5233
Wailea 25/1395 | 38.6619 | 35.159 | 33.8801 | 23.1236 | 23.3606
Wailea 25/1396 | 71.3669 | 64.9007 | 62.54 | 42.6844 | 43.1218
Wailea 25/1517 | 219.9195 | 199.9938 | 192.7193 | 131.5336 | 132.8814
Wailea 25/1518 | 133.1358 | 121.0731 | 116.6692 | 79.6284 | 80.4443
Wailuku 3/1290 | 355.0827 | 322.9105 | 311.1651 | 212.3746 | 214.5507
Wailuku 3/1447 | 236.7847 | 215.3309 | 207.4985 | 141.6207 | 143.0719
Wailuku 3/4031 | 45.5295 | 41.4043 | 39.8983 | 27.2311 | 27.5102
Wailuku 3/4037 | 71.2233 | 64.7701 | 62.4142 | 42.5986 | 43.0351
Wailuku Heights 18/493 | 69.9582 | 63.6197 | 61.3056 | 41.8419 | 42.2707
Wailuku Heights 18/529 | 44.9099 | 40.8409 | 39.3553 | 26.8606 | 27.1358

## Lanai Circuit DER Growth
Return to Assumptions Summary
Lana‘i Adjusted DER Growth by Circuit - Base Forecast
The Adjusted DER Growth by Circuit shows the annual DER growth by circuit. The forecast is shown by circuit (or feeder) peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth (kW)
Circuit | 2021 | 2022 | 2023 | 2024 | 2025
Miki Basin PP 302/1208 | 14.3986 | 12.7988 | 41.996 | 7.9992 | 9.5991
Miki Basin PP 302/1210 | 4.9564 | 4.4057 | 14.4563 | 2.7536 | 3.3043
Miki Basin PP 302/1212 | 16.6449 | 14.7955 | 48.5477 | 9.2472 | 11.0966

## Molokai Circuit DER Growth
Return to Assumptions Summary
Moloka‘i Adjusted DER Growth by Circuit - Base Forecast
The Adjusted DER Growth by Circuit shows the annual DER growth by circuit. The forecast is shown by circuit (or feeder) peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth (kW)
Circuit | 2021 | 2022 | 2023 | 2024 | 2025
Palaau PP 81/105A | 53.0181 | 33.5557 | 55.0314 | 17.449 | 16.1068
Palaau PP 81/106B | 14.0818 | 8.9126 | 14.6166 | 4.6345 | 4.278
Palaau PP 81/109B | 7.1955 | 4.5541 | 7.4688 | 2.3681 | 2.186
Palaau PP 81/110B | 13.888 | 8.7899 | 14.4154 | 4.5707 | 4.2191
Palaau PP 81/111A | 306.3602 | 35.671 | 58.5005 | 18.5489 | 17.1221
Puunana 80/1466 | 2.1826 | 1.3814 | 2.2655 | 0.71834 | 0.66308
Puunana 80/1467 | 10.6539 | 6.743 | 11.0585 | 3.5064 | 3.2366
Puunana 80/1468 | 0.61972 | 0.39223 | 0.64326 | 0.20396 | 0.18827

## Summary HC Results
Return to Assumptions Summary
Summary of Hosting Capacity Results - Base Forecast
These tables summarize the Hosting Capacity Results for all islands.
Island | Total Circuits | Existing Hosting Capacity Satisfies Need (Analysis Not Required) | Forecasted DER > Hosting Capacity (Analysis Required)
O‘ahu | 384 | 350 | 34
Hawai‘i Island | 137 | 95 | 42
Maui Island | 88 | 58 | 30
Lana‘i | 3 | 1 | 2
Moloka‘i | 8 | 5 | 3
Total (All Islands) | 620 | 509 | 111
Island | Grid Needs Not Required |  | Grid Needs Identified
| Existing HC Satisfies Need | Updated HC (w/o Mods) Satisfies Need | Updated HC (w/ Mods) Satisfies Need | Solution Option Required | Total
O‘ahu | 350 | 22 | 6 | 6 | 384
Hawai‘i Island | 95 | 21 | 19 | 2 | 137
Maui Island* | 58 | 15 | 12 | 3 | 88
Lana‘i | 1 | 0 | 0 | 2 | 3
Moloka‘i | 5 | 0 | 0 | 3 | 8
Total (All Islands) | 509 | 58 | 37 | 16 | 620
Figure 8 Data | [5 empty] | Figure 8: Summary of Hosting Capacity Results (% of Total Circuits)
Island | Existing HC Satisfies Need | Updated HC (w/o Mods) Satisfies Need | Updated HC (w/ Mods) Satisfies Need | Solution Option Required | Total
O‘ahu | 91.15% | 5.729% | 1.562% | 1.562% | 100%
Hawai‘i Island | 69.34% | 15.33% | 13.87% | 1.46% | 100%
Maui Island* | 65.91% | 17.05% | 13.64% | 3.409% | 100%
Lana‘i | 33.33% | 0% | 0% | 66.67% | 100%
Moloka‘i | 62.5% | 0% | 0% | 37.5% | 100%
Total (All Islands) | 82.1% | 9.355% | 5.968% | 2.581% | 100%

## Oahu HC Results
Return to Assumptions Summary
O‘ahu Hosting Capacity Analysis Results by Circuit - Base Forecast
The Hosting Capacity Analysis Results by Circuit shows the Existing Hosting Capacity (HC) rating compared to the Total 2025 DER Forecast. The Total 2025 DER is the total anticipated DER in year 2025. Circuits with existing hosting capacity able to accommodate the Total 2025 DER are marked with an “X” in the Existing HC Satisfies Need column. Circuits with updated hosting capacity able to accommodate the Total 2025 DER without any modifications are marked with an “X” in the Updated HC (w/o Mods) Satisfies Need column. Circuits with updated hosting capacity and modifications (non-infrastructure investment solutions) able to accommodate the Total 2025 DER are marked with an “X” in the Updated HC (w/ Mods) Satisfies Needs column. Circuits that require infrastructure investment solutions are marked with an "X" in the Solution Option Required column. Additional details for these circuits are shown in the Grid Needs Assessment (GNA) tables. The Circuit Count provides a summary of the hosting caapcity results. The Hosting Capacity Increase (kW) is an estimate of the increase in hosting capacity due to the total updated hosting capacity available for all circuits as a result of this analysis. The Total 2025 DER forecast and hosting capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
Circuit Name | Total 2025 DER (kW) | Existing HC (kW) | Existing HC Satisfies Need | Updated HC (kW) | Updated HC (w/o Mods) Satisfies Need | Updated HC (w/ Mods) Satisfies Need | Solution Option Required | HC Increase (kW) | Circuit Count | Total
AALA | 1761.797 | 6044 | x |  |  |  |  | 0 | Total Circuits | 384
AALAPAPA | 3647.405 | 4786 | x |  |  |  |  | 0 | Existing HC Satisfies Need | 350
AHUA | 1810.073 | 1561 |  | 5210 | x |  |  | 249.073 | Updated HC (w/o Modifications) | 22
AHUI | 0 | 361 | x |  |  |  |  | 0 | Updated HC (w Modifications) | 6
AIEA | 3896.209 | 3601 |  | 5700 |  | x |  | 295.209 | Solution Option Required | 6
AIEA 2 | 552.835 | 2986 | x |  |  |  |  | 0
AIEA 3 | 301.218 | 1008 | x |  |  |  |  | 0
AINA KOA | 3512.682 | 2951 |  | 4080 |  |  | x | 561.682
AINONI | 1260.003 | 1500 | x |  |  |  |  | 0 | Hosting Capacity Increase (kW) | 27578.847
AIRPORT | 2471.314 | 5669 | x |  |  |  |  | 0
AIRPORT 1 | 100 | 2724 | x |  |  |  |  | 0
AIRPORT 2 | 100 | 1716 | x |  |  |  |  | 0
ALA MOANA | 454.784 | 6272 | x |  |  |  |  | 0
ALEWA | 470.885 | 580 | x |  |  |  |  | 0
ALIAMANU | 4432.394 | 6346 | x |  |  |  |  | 0
ANOI | 4479.363 | 3794 |  | 5140 | x |  |  | 685.363
ANUU | 4152.953 | 4073 |  | 4690 | x |  |  | 79.953
ARCHER 1 | 400 | 2402 | x |  |  |  |  | 0
ARCHER 2 | 700 | 3003 | x |  |  |  |  | 0
ARCHER 3 | 2985.811 | 7277 | x |  |  |  |  | 0
ARCHER 4 | 378 | 5293 | x |  |  |  |  | 0
AUDITORIUM | 570.728 | 4589 | x |  |  |  |  | 0
BARBERS PT | 1380.81 | 7170 | x |  |  |  |  | 0
BAY DR | 1079.711 | 1424 | x |  |  |  |  | 0
BEACH LOTS | 4584.153 | 4712 | x |  |  |  |  | 0
BECKLEY | 271.048 | 304 | x |  |  |  |  | 0
BLACK PT | 675.618 | 1007 | x |  |  |  |  | 0
BWS | 922.634 | 4190 | x |  |  |  |  | 0
CARLOS LONG | 3231.086 | 3984 | x |  |  |  |  | 0
CASTNER | 2203.967 | 6569 | x |  |  |  |  | 0
CEIP 3 | 3120.18 | 6243 | x |  |  |  |  | 0
CEIP 4 | 592.053 | 1478 | x |  |  |  |  | 0
CKT 10 | 568.535 | 2068 | x |  |  |  |  | 0
CKT 12 | 100 | 3107 | x |  |  |  |  | 0
CKT 16 | 7591.326 | 6611 |  | 10012 | x |  |  | 980.326
CKT 18 | 1132.951 | 4151 | x |  |  |  |  | 0
CKT 6 | 848.09 | 2806 | x |  |  |  |  | 0
CKT 7 | 971.018 | 4397 | x |  |  |  |  | 0
CKT 8 | 0 | 1403 | x |  |  |  |  | 0
COCONUT GROVE | 1213.957 | 1457 | x |  |  |  |  | 0
DAIRYMENS | 449.105 | 2649 | x |  |  |  |  | 0
DE RUSSY | 600 | 3126 | x |  |  |  |  | 0
DEPOT RD | 1332.237 | 2327 | x |  |  |  |  | 0
DIAMOND HEAD | 1985.33 | 1452 |  | 3280 |  | x |  | 533.33
DOLE 1 | 2453.158 | 5673 | x |  |  |  |  | 0
EKEKELA | 920.317 | 1070 | x |  |  |  |  | 0
ENA 1 | 306.268 | 3559 | x |  |  |  |  | 0
ENA 2 | 7.765 | 4529 | x |  |  |  |  | 0
ENCHANTED LAKES | 4263.593 | 5155 | x |  |  |  |  | 0
EWA BEACH 1 | 4708.816 | 6550 | x |  |  |  |  | 0
EWA BEACH 2 | 3408.07 | 4257 | x |  |  |  |  | 0
EWA BEACH 3 | 3943.846 | 4029 | x |  |  |  |  | 0
EWA BEACH 4 | 5969.706 | 5966 |  | 8046 | x |  |  | 3.706
EWA NUI 1 | 3717.771 | 6430 | x |  |  |  |  | 0
EWA NUI 2 | 6239.402 | 6024 |  | 8089 | x |  |  | 215.402
FARMERS RD | 1345.711 | 1411 | x |  |  |  |  | 0
FORT ST | 693.061 | 4340 | x |  |  |  |  | 0
FORT ST 1 | 303.66 | 3014 | x |  |  |  |  | 0
FORT ST 2 | 500.527 | 3672 | x |  |  |  |  | 0
FORT ST 3 | 419.258 | 3667 | x |  |  |  |  | 0
FORT ST 4 | 607.41 | 2895 | x |  |  |  |  | 0
FORT WEAVER 1 | 3970.279 | 5458 | x |  |  |  |  | 0
FORT WEAVER 2 | 5549.183 | 6321 | x |  |  |  |  | 0
FORT WEAVER 3 | 4972.813 | 5950 | x |  |  |  |  | 0
FORT WEAVER 4 | 2340.656 | 4293 | x |  |  |  |  | 0
HAHAIONE | 2792.213 | 3366 | x |  |  |  |  | 0
HALA 1 | 2576.754 | 4003 | x |  |  |  |  | 0
HALA 2 | 1845.359 | 4308 | x |  |  |  |  | 0
HALA 3 | 3427.51 | 4824 | x |  |  |  |  | 0
HALA 4 | 1795.285 | 4351 | x |  |  |  |  | 0
HALAWA | 2733.086 | 6775 | x |  |  |  |  | 0
HALEKOU | 3854.383 | 5289 | x |  |  |  |  | 0
HANUA 1 | 0 | 0 | x |  |  |  |  | 0
HANUA 2 | 0 | 0 | x |  |  |  |  | 0
HAUULA | 6833.55 | 2802 |  | 9310.9 | x |  |  | 4031.55
HAWN PINE | 1653.537 | 5841 | x |  |  |  |  | 0
HAWN VILLAGE 1 | 201.052 | 3528 | x |  |  |  |  | 0
HAWN VILLAGE 2 | 341.756 | 2673 | x |  |  |  |  | 0
HEEIA | 4187.424 | 5140 | x |  |  |  |  | 0
HEIGHTS | 1226.635 | 1145 |  | 1397.5 | x |  |  | 81.635
HELEMANO | 2903.045 | 4406 | x |  |  |  |  | 0
HIGHLANDS | 4369.925 | 6162 | x |  |  |  |  | 0
HIKINA | 185.603 | 220 | x |  |  |  |  | 0
HILA 1 | 1013.756 | 1968 | x |  |  |  |  | 0
HILA 2 | 2527.291 | 3688 | x |  |  |  |  | 0
HILA 3 | 1668.033 | 5288 | x |  |  |  |  | 0
HILA 4 | 400 | 0 |  | 2323 | x |  |  | 400
HILA 5 | 2104.527 | 6597 | x |  |  |  |  | 0
HILA 6 | 0 | 0 | x |  |  |  |  | 0
HOAEAE 1 | 4794.262 | 5113 | x |  |  |  |  | 0
HOAEAE 2 | 1007.462 | 2163 | x |  |  |  |  | 0
HOAEAE 3 | 2681.819 | 2488 |  | 4038 | x |  |  | 193.819
HOUGHTAILING | 1157.559 | 5510 | x |  |  |  |  | 0
HUNAKAI | 919.336 | 1508 | x |  |  |  |  | 0
ILANIWAI | 392.073 | 3605 | x |  |  |  |  | 0
ILIAINA | 1920.309 | 2541 | x |  |  |  |  | 0
ILIKAI | 218.249 | 4283 | x |  |  |  |  | 0
INDUSTRIAL | 3897.093 | 7546 | x |  |  |  |  | 0
IWILEI 1 11KV | 1631.383 | 7190 | x |  |  |  |  | 0
IWILEI 13 | 369.58 | 3979 | x |  |  |  |  | 0
IWILEI 9 | 0 | 4164 | x |  |  |  |  | 0
KAALAKEI | 3818.558 | 5132 | x |  |  |  |  | 0
KAENA PT | 2210.483 | 2739 | x |  |  |  |  | 0
KAHAI | 3388.496 | 6866 | x |  |  |  |  | 0
KAHALA | 1717.492 | 1976 | x |  |  |  |  | 0
KAHALA 3 | 6315.024 | 1609 |  | 7269 | x |  |  | 4706.024
KAHALA MALL | 2087.12 | 2970 | x |  |  |  |  | 0
KAHALOA | 1256.25 | 1407 | x |  |  |  |  | 0
KAHE | 3420.198 | 5684 | x |  |  |  |  | 0
KAHUKU | 2704.787 | 2422 |  | 3510 | x |  |  | 282.787
KAI-HARDING | 411.801 | 471 | x |  |  |  |  | 0
KAI-KAIMUKI | 783.539 | 1162 | x |  |  |  |  | 0
KAILUA 1 | 3141.256 | 3746 | x |  |  |  |  | 0
KAILUA 2 | 5173.603 | 7039 | x |  |  |  |  | 0
KAILUA HTS | 4585.341 | 5755 | x |  |  |  |  | 0
KAINALU | 2199.462 | 1047 |  | 2300 |  |  | x | 1152.462
KAI-WAIALAE | 1064.878 | 1646 | x |  |  |  |  | 0
KAI-WILHELMINA | 599.165 | 930 | x |  |  |  |  | 0
KAKAAKO 5 | 81.897 | 430 | x |  |  |  |  | 0
KAKAAKO 6 | 0 | 1646 | x |  |  |  |  | 0
KAKAAKO 8 | 1856.801 | 3781 | x |  |  |  |  | 0
KAKAAKO 9 | 821.047 | 7502 | x |  |  |  |  | 0
KALAHEO | 1287.328 | 1462 | x |  |  |  |  | 0
KALAHEO 1 | 341 | 2344 | x |  |  |  |  | 0
KALAHEO 2 | 0 | 0 | x |  |  |  |  | 0
KALAKAUA | 359.642 | 4831 | x |  |  |  |  | 0
KALAMA | 1080.892 | 1277 | x |  |  |  |  | 0
KALIA | 0 | 5654 | x |  |  |  |  | 0
KALIHI | 113.19 | 5187 | x |  |  |  |  | 0
KALIHI KAI | 503.635 | 1604 | x |  |  |  |  | 0
KALIHI ST | 888.404 | 1021 | x |  |  |  |  | 0
KALIHI UKA | 460.956 | 1278 | x |  |  |  |  | 0
KALIHI VALLEY | 736.677 | 1701 | x |  |  |  |  | 0
KALOI 1 | 1114.56 | 612 |  | 2979 | x |  |  | 502.56
KAM HWY | 1349.618 | 5123 | x |  |  |  |  | 0
KAM IV | 1000.447 | 1322 | x |  |  |  |  | 0
KAM TERRACE | 1205.277 | 1323 | x |  |  |  |  | 0
KAMAKEE | 579.931 | 2456 | x |  |  |  |  | 0
KAMANI | 461.2 | 1505 | x |  |  |  |  | 0
KAMOKILA 1 | 2989.53 | 4660 | x |  |  |  |  | 0
KAMOKILA 2 | 2544.468 | 4541 | x |  |  |  |  | 0
KAMOKILA 3 | 2671.21 | 2937 | x |  |  |  |  | 0
KAMOKILA 4 | 3183.14 | 3966 | x |  |  |  |  | 0
KAMOKILA 5 | 2421.026 | 6548 | x |  |  |  |  | 0
KAMOKILA 6 | 1518.588 | 3259 | x |  |  |  |  | 0
KAMOKU 10 | 506.78 | 8363 | x |  |  |  |  | 0
KAMOKU 9 | 240.56 | 6223 | x |  |  |  |  | 0
KANAINA | 3829.129 | 6528 | x |  |  |  |  | 0
KANEKAPOLEI | 619.843 | 3308 | x |  |  |  |  | 0
KANEOHE 5 | 2212.535 | 2804 | x |  |  |  |  | 0
KANEOHE 6 | 2538.977 | 5977 | x |  |  |  |  | 0
KAONOHI 1 | 1092.558 | 3482 | x |  |  |  |  | 0
KAONOHI 2 | 3346.666 | 5066 | x |  |  |  |  | 0
KAONOHI 3 | 851.063 | 4965 | x |  |  |  |  | 0
KAONOHI 4 | 636.669 | 4030 | x |  |  |  |  | 0
KAPAHULU 1 | 145.798 | 1355 | x |  |  |  |  | 0
KAPAHULU 2 | 0 | 5774 | x |  |  |  |  | 0
KAPAHULU 3 | 205.87 | 4879 | x |  |  |  |  | 0
KAPAHULU 4 | 113.802 | 3629 | x |  |  |  |  | 0
KAPALAMA | 312.278 | 587 | x |  |  |  |  | 0
KAP-HARDING | 878.088 | 1157 | x |  |  |  |  | 0
KAPIOLANI 1 | 1401.409 | 4867 | x |  |  |  |  | 0
KAPIOLANI 2 | 1787.652 | 5354 | x |  |  |  |  | 0
KAPIOLANI 3 | 1272.344 | 4056 | x |  |  |  |  | 0
KAP-KAIMUKI | 229.575 | 1911 | x |  |  |  |  | 0
KAPOLEI 1 | 105.52 | 644 | x |  |  |  |  | 0
KAPOLEI 2 | 2138.717 | 4169 | x |  |  |  |  | 0
KAPOLEI 3 | 1001.598 | 3780 | x |  |  |  |  | 0
KAPOLEI 4 | 6733.895 | 2966 |  | 6971 | x |  |  | 3767.895
KAP-WAIALAE | 503.96 | 1032 | x |  |  |  |  | 0
KAUHALE | 1120.558 | 6157 | x |  |  |  |  | 0
KAWAILOA | 1458.5 | 1133 |  | 2467.46 |  | x |  | 325.5
KAWELA | 3301.53 | 4800 | x |  |  |  |  | 0
KEALAOLU | 416.046 | 1120 | x |  |  |  |  | 0
KEAWE | 1050.749 | 4502 | x |  |  |  |  | 0
KEEHI 1 | 510.495 | 2912 | x |  |  |  |  | 0
KEEHI 5 | 1176.156 | 3166 | x |  |  |  |  | 0
KEEHI 6 | 920.125 | 4074 | x |  |  |  |  | 0
KEEHI 7 | 1029.9 | 2866 | x |  |  |  |  | 0
KEEHI 8 | 900 | 1766 | x |  |  |  |  | 0
KEOLU DR | 2620.168 | 4497 | x |  |  |  |  | 0
KEWALO | 7285.366 | 7024 |  | 11693 | x |  |  | 261.366
KEWALO 1 | 270.565 | 3591 | x |  |  |  |  | 0
KEWALO 2 | 257.792 | 4809 | x |  |  |  |  | 0
KEWALO 3 | 0 | 73 | x |  |  |  |  | 0
KEWALO 4 | 319.138 | 2953 | x |  |  |  |  | 0
KEWALO 5 | 500 | 11185 | x |  |  |  |  | 0
KEWALO 6 | 370 | 5907 | x |  |  |  |  | 0
KEWALO 7 | 0 | 0 | x |  |  |  |  | 0
KILAUEA 12KV | 2140.051 | 6299 | x |  |  |  |  | 0
KILAUEA 4KV | 1011.748 | 962 |  | 1300 |  |  | x | 49.748
KIPAPA | 1090.348 | 3487 | x |  |  |  |  | 0
KO OLINA 1 | 645.694 | 8395 | x |  |  |  |  | 0
KO OLINA 2 | 0 | 84 | x |  |  |  |  | 0
KO OLINA 3 | 200 | 4546 | x |  |  |  |  | 0
KOKOHEAD | 2517.011 | 3252 | x |  |  |  |  | 0
KOLOA | 1043.847 | 1281 | x |  |  |  |  | 0
KONA ST | 0 | 893 | x |  |  |  |  | 0
KUAHELANI 1 | 2696.152 | 4897 | x |  |  |  |  | 0
KUAHELANI 2 | 1868.144 | 4138 | x |  |  |  |  | 0
KUAHELANI 3 | 3814.941 | 7671 | x |  |  |  |  | 0
KUAHELANI 4 | 5617.094 | 10634 | x |  |  |  |  | 0
KUAKINI | 146.451 | 952 | x |  |  |  |  | 0
KUAPA 1 | 2093.332 | 4410 | x |  |  |  |  | 0
KUAPA 2 | 1748.132 | 1891 | x |  |  |  |  | 0
KUAPA 3 | 3053.219 | 4110 | x |  |  |  |  | 0
KUAPA 4 | 2462.883 | 3136 | x |  |  |  |  | 0
KUHIO | 280.061 | 505 | x |  |  |  |  | 0
KUHIO 1 | 78.548 | 5370 | x |  |  |  |  | 0
KUHIO 2 | 500 | 983 | x |  |  |  |  | 0
KUHIO 3 | 102.44 | 3562 | x |  |  |  |  | 0
KUHIO 4 | 350.209 | 3627 | x |  |  |  |  | 0
KUILIMA 1 | 1196.814 | 1524 | x |  |  |  |  | 0
KUNIA | 684.24 | 1711 | x |  |  |  |  | 0
KUNIA MAKAI 1 | 2306.981 | 3433 | x |  |  |  |  | 0
KUNIA MAKAI 2 | 5344.783 | 7394 | x |  |  |  |  | 0
KUNIA MAKAI 3 | 3663.804 | 5979 | x |  |  |  |  | 0
KUNIA MAKAI 4 | 1511.145 | 2007 | x |  |  |  |  | 0
LAGOON | 892.086 | 8176 | x |  |  |  |  | 0
LAKESIDE 1 | 2711.173 | 4373 | x |  |  |  |  | 0
LAKESIDE 2 | 963.671 | 2008 | x |  |  |  |  | 0
LAKESIDE 3 | 1756.254 | 5447 | x |  |  |  |  | 0
LAKESIDE 4 | 1990.207 | 3541 | x |  |  |  |  | 0
LANIKAI | 7.758 | 179 | x |  |  |  |  | 0
LAULIMA | 2605.128 | 4187 | x |  |  |  |  | 0
LEAHI | 2923.665 | 5460 | x |  |  |  |  | 0
LEOMELE | 2279.611 | 2938 | x |  |  |  |  | 0
LEOOLE | 2336.938 | 3527 | x |  |  |  |  | 0
LIBERTY HOUSE | 175 | 2502 | x |  |  |  |  | 0
LIGHTHOUSE | 1330.513 | 7972 | x |  |  |  |  | 0
LIKELIKE | 444.462 | 680 | x |  |  |  |  | 0
LILIHA MAKAI | 61.279 | 190 | x |  |  |  |  | 0
LOWREY | 1111.956 | 1129 | x |  |  |  |  | 0
LUAWAI | 3385.921 | 7351 | x |  |  |  |  | 0
LUMIAUAU | 1807.106 | 4579 | x |  |  |  |  | 0
MACHADO ST | 690.487 | 736 | x |  |  |  |  | 0
MAHUKONA | 1203.176 | 4899 | x |  |  |  |  | 0
MAKAHA | 4001.081 | 5685 | x |  |  |  |  | 0
MAKAHA VALLEY | 994.17 | 1725 | x |  |  |  |  | 0
MAKAKILO 1 | 3500.954 | 3988 | x |  |  |  |  | 0
MAKAKILO 2 | 9312.231 | 8472 |  | 10570 |  | x |  | 840.231
MAKAKILO 3 | 3622.776 | 5277 | x |  |  |  |  | 0
MAKAKILO 4 | 1296.292 | 1813 | x |  |  |  |  | 0
MAKALAPA-MOANALUA | 3204.883 | 4285 | x |  |  |  |  | 0
MAKALOA | 385.684 | 4602 | x |  |  |  |  | 0
MALAKOLE | 0 | 0 | x |  |  |  |  | 0
MALAKOLE 4 | 5437.68 | 6087 | x |  |  |  |  | 0
MANAGERS | 689.504 | 1478 | x |  |  |  |  | 0
MANOA 1 | 2101.775 | 2732 | x |  |  |  |  | 0
MANOA 2 | 1010.335 | 1089 | x |  |  |  |  | 0
MANOA 3 | 2712.258 | 4168 | x |  |  |  |  | 0
MANOA 4 | 0 | 266 | x |  |  |  |  | 0
MANOA-MCCULLY | 633.026 | 4259 | x |  |  |  |  | 0
MANOA-PIIKOI | 1872.599 | 1553 |  | 2090 |  |  | x | 319.599
MAPUNAPUNA | 750.673 | 371 |  | 3631 | x |  |  | 379.673
MAPUNAPUNA-MOANALUA | 1900.269 | 2345 | x |  |  |  |  | 0
MAUKA | 10010.065 | 8350 |  | 10283 |  |  | x | 1660.065
MAUNALANI | 1824.826 | 2057 | x |  |  |  |  | 0
MAUNAWILI | 0 | 108 | x |  |  |  |  | 0
MCCULLY 1 | 1059.378 | 7195 | x |  |  |  |  | 0
MCCULLY 3 | 1981.04 | 5548 | x |  |  |  |  | 0
MCCULLY 5 | 786.626 | 3836 | x |  |  |  |  | 0
MIKILUA 1 | 2223.412 | 6431 | x |  |  |  |  | 0
MIKILUA 3 | 5152.28 | 4761 |  | 5440 | x |  |  | 391.28
MIKILUA 4 | 6244.546 | 3514 |  | 7653 | x |  |  | 2730.546
MIKILUA 5 | 6999.889 | 7382 | x |  |  |  |  | 0
MILILANI 1 | 2810.999 | 4605 | x |  |  |  |  | 0
MILILANI 2 | 1653.08 | 5475 | x |  |  |  |  | 0
MILILANI 3 | 2193.475 | 3763 | x |  |  |  |  | 0
MILILANI 4 | 6014.36 | 7449 | x |  |  |  |  | 0
MOILIILI 1 | 1436.553 | 4596 | x |  |  |  |  | 0
MOILIILI 2 | 706.757 | 3937 | x |  |  |  |  | 0
MOKAUEA | 510.967 | 2933 | x |  |  |  |  | 0
MOKUOLA | 3243.631 | 6033 | x |  |  |  |  | 0
MOKUONE 1 | 0 | 4641 | x |  |  |  |  | 0
MOKUONE 2 | 1467.92 | 4421 | x |  |  |  |  | 0
NIU | 3249.304 | 4171 | x |  |  |  |  | 0
NUMANA | 386.862 | 1154 | x |  |  |  |  | 0
NUUANU | 701.831 | 719 | x |  |  |  |  | 0
NUUANU 2 | 2088.531 | 5155 | x |  |  |  |  | 0
NUUANU 3 | 3819.472 | 6965 | x |  |  |  |  | 0
OCEAN POINTE 1 | 4977.228 | 5876 | x |  |  |  |  | 0
OCEAN POINTE 2 | 4414.104 | 5280 | x |  |  |  |  | 0
OCEAN POINTE 3 | 3412.682 | 5444 | x |  |  |  |  | 0
OCEAN POINTE 4 | 1401.258 | 1362 |  | 1713 | x |  |  | 39.258
OLOMANA | 2032.996 | 2936 | x |  |  |  |  | 0
ONEAWA | 935.925 | 908 |  | 1860 |  | x |  | 27.925
PAHIA | 2090.522 | 1505 |  | 4730 | x |  |  | 585.522
PAIWA | 1660.141 | 3378 | x |  |  |  |  | 0
PALEKA | 2250.271 | 2584 | x |  |  |  |  | 0
PALI | 3457.523 | 4764 | x |  |  |  |  | 0
PAOAKALANI | 1222.095 | 5271 | x |  |  |  |  | 0
PAUOA 1 | 1818.686 | 2333 | x |  |  |  |  | 0
PAUOA 2 | 3973.068 | 4522 | x |  |  |  |  | 0
PAWAA KAI | 635.949 | 2667 | x |  |  |  |  | 0
PAWAINA | 1523.215 | 1824 | x |  |  |  |  | 0
PEARL CITY 1 | 2126.805 | 5934 | x |  |  |  |  | 0
PEARL CITY 2 | 1820.672 | 5588 | x |  |  |  |  | 0
PENINSULA | 2458.45 | 6106 | x |  |  |  |  | 0
PENSACOLA | 1924.071 | 3860 | x |  |  |  |  | 0
PIIKOI | 644.549 | 4017 | x |  |  |  |  | 0
PIIKOI 7 | 978.63 | 2773 | x |  |  |  |  | 0
PIIKOI 8 | 2368.024 | 1993 |  | 3469 |  |  | x | 375.024
POAMOHO | 0 | 0 | x |  |  |  |  | 0
POHAKUPU 4 | 3291.853 | 4054 | x |  |  |  |  | 0
PORTLOCK | 2765.089 | 4113 | x |  |  |  |  | 0
PUNALUU | 2679.084 | 3552 | x |  |  |  |  | 0
PUNCHBOWL | 578.36 | 656 | x |  |  |  |  | 0
PUOHALA 1 | 2200.014 | 4019 | x |  |  |  |  | 0
PUOHALA 2 | 5336.87 | 7179 | x |  |  |  |  | 0
PUUHALE | 1649.714 | 2526 | x |  |  |  |  | 0
PUUNUI | 1147.829 | 1354 | x |  |  |  |  | 0
QUEEN ST | 471.518 | 2128 | x |  |  |  |  | 0
QUEENS 1 | 2799.709 | 3735 | x |  |  |  |  | 0
QUEENS 2 | 1613.868 | 1722 | x |  |  |  |  | 0
RUGER | 485.707 | 1010 | x |  |  |  |  | 0
SAND ISLAND | 640.112 | 6808 | x |  |  |  |  | 0
SAND ISLAND 1 | 460 | 6285 | x |  |  |  |  | 0
SAND ISLAND 2 | 463 | 3034 | x |  |  |  |  | 0
SCHOOL ST | 2019.677 | 3452 | x |  |  |  |  | 0
SCHOOL ST 3 | 1982.779 | 5183 | x |  |  |  |  | 0
SHAFTER | 822.14 | 3086 | x |  |  |  |  | 0
SHERATON 1 | 209.166 | 1536 | x |  |  |  |  | 0
SHERATON 2 | 64.588 | 4551 | x |  |  |  |  | 0
SHOPPING CTR | 1444.49 | 4165 | x |  |  |  |  | 0
SOUTH RAMP 1 | 2274.39 | 3765 | x |  |  |  |  | 0
ST LOUIS | 2596.61 | 2853 | x |  |  |  |  | 0
ST LOUIS HTS | 127.565 | 337 | x |  |  |  |  | 0
THURSTON | 1265.277 | 4669 | x |  |  |  |  | 0
TOWN | 2.433 | 144 | x |  |  |  |  | 0
UALENA | 1674.513 | 5228 | x |  |  |  |  | 0
UPLANDS | 1156.569 | 1379 | x |  |  |  |  | 0
UWAPO 1 | 4219.023 | 5433 | x |  |  |  |  | 0
UWAPO 2 | 1357.577 | 1637 | x |  |  |  |  | 0
UWAPO 3 | 4304.467 | 5881 | x |  |  |  |  | 0
UWAPO 4 | 38.04 | 924 | x |  |  |  |  | 0
WAHIAWA HTS | 4060.705 | 4206 | x |  |  |  |  | 0
WAHIAWA PROPER | 1167.331 | 5964 | x |  |  |  |  | 0
WAIAKAMILO 1 | 476.449 | 2530 | x |  |  |  |  | 0
WAIAKAMILO 2 | 1209.332 | 5490 | x |  |  |  |  | 0
WAIAKAMILO 3 | 2451.245 | 5827 | x |  |  |  |  | 0
WAIAKAMILO 4 | 1685.117 | 3697 | x |  |  |  |  | 0
WAIAKAMILO-IWILEI | 568.251 | 959 | x |  |  |  |  | 0
WAIAKAMILO-KAPALAMA | 2932.354 | 9020 | x |  |  |  |  | 0
WAIALAE NUI | 2268.187 | 3646 | x |  |  |  |  | 0
WAIALAE SC | 0 | 746 | x |  |  |  |  | 0
WAIALUA | 2438.891 | 1711 |  | 3301.66 |  | x |  | 727.891
WAIAWA 1 | 4560.107 | 6447 | x |  |  |  |  | 0
WAIAWA 2 | 3266.92 | 9144 | x |  |  |  |  | 0
WAIAWA 3 | 3390.424 | 7605 | x |  |  |  |  | 0
WAIAWA 4 | 2210.679 | 4257 | x |  |  |  |  | 0
WAIHEE 1 | 3110.148 | 3804 | x |  |  |  |  | 0
WAIHEE 2 | 1854.361 | 2101 | x |  |  |  |  | 0
WAIHEE 3 | 709.425 | 660 |  | 1120 | x |  |  | 49.425
WAIHEE 4 | 3546.988 | 4189 | x |  |  |  |  | 0
WAIKELE CTR | 100 | 3133 | x |  |  |  |  | 0
WAIKIKI 1 | 305.667 | 1844 | x |  |  |  |  | 0
WAIKIKI 2 | 200 | 6144 | x |  |  |  |  | 0
WAIKIKI 3 | 172.607 | 6602 | x |  |  |  |  | 0
WAIKIKI 4 | 270.696 | 6104 | x |  |  |  |  | 0
WAIKIKI 5 | 593.516 | 3888 | x |  |  |  |  | 0
WAIKIKI 6 | 555.408 | 4256 | x |  |  |  |  | 0
WAILANI | 1399.426 | 2982 | x |  |  |  |  | 0
WAILUPE | 6418.609 | 6579 | x |  |  |  |  | 0
WAIMALU 1 | 3593.047 | 6268 | x |  |  |  |  | 0
WAIMALU 2 | 2699.722 | 4994 | x |  |  |  |  | 0
WAIMALU 3 | 5336.889 | 5984 | x |  |  |  |  | 0
WAIMALU 4 | 2377.319 | 3523 | x |  |  |  |  | 0
WAIMANALO | 1755.415 | 2248 | x |  |  |  |  | 0
WAIMANO 5 | 1726.987 | 2078 | x |  |  |  |  | 0
WAIMANO 6 | 2147.992 | 4506 | x |  |  |  |  | 0
WAIMANO HOME RD | 4155.928 | 5099 | x |  |  |  |  | 0
WAIMEA 1 | 669.162 | 788 | x |  |  |  |  | 0
WAIMEA 2 | 2640.691 | 3168 | x |  |  |  |  | 0
WAIOMAO | 4137.734 | 5743 | x |  |  |  |  | 0
WAIPAHU | 7139.494 | 8874 | x |  |  |  |  | 0
WAIPIO 1 | 1922.28 | 4249 | x |  |  |  |  | 0
WAIPIO 2 | 1237.561 | 4040 | x |  |  |  |  | 0
WAIWAI | 947.01 | 2823 | x |  |  |  |  | 0
WAI-WILHELMINA | 1223.464 | 1376 | x |  |  |  |  | 0
WHITMORE | 63.958 | 308 | x |  |  |  |  | 0
WILIWILI | 2094.74 | 2293 | x |  |  |  |  | 0
WILIWILI 2 | 2219.018 | 2126 |  | 2566 | x |  |  | 93.018
WOODLAWN | 1005.227 | 1242 | x |  |  |  |  | 0

## Hawaii Island HC Results
Return to Assumptions Summary
Hawai‘i Island Hosting Capacity Analysis Results by Circuit - Base Forecast
The Hosting Capacity Analysis Results by Circuit shows the Existing Hosting Capacity (HC) rating compared to the Total 2025 DER Forecast. The Total 2025 DER is the total anticipated DER in year 2025. Circuits with existing hosting capacity able to accommodate the Total 2025 DER are marked with an “X” in the Existing HC Satisfies Need column. Circuits with updated hosting capacity able to accommodate the Total 2025 DER without any modifications are marked with an “X” in the Updated HC (w/o Mods) Satisfies Need column. Circuits with updated hosting capacity and modifications (non-infrastructure investment solutions) able to accommodate the Total 2025 DER are marked with an “X” in the Updated HC (w/ Mods) Satisfies Needs column. Circuits that require infrastructure investment solutions are marked with an "X" in the Solution Option Required column. Additional details for these circuits are shown in the Grid Needs Assessment (GNA) tables. The Circuit Count provides a summary of the hosting caapcity results. The Hosting Capacity Increase (kW) is an estimate of the increase in hosting capacity due to the total updated hosting capacity available for all circuits as a result of this analysis. The Total 2025 DER forecast and hosting capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
Circuit Name | Total 2025 DER (kW) | Existing HC (kW) | Existing HC Satisfies Need | Updated HC (kW) | Updated HC (w/o Mods) Satisfies Need | Updated HC (w/ Mods) Satisfies Need | Solution Option Required | HC Increase (kW) | Circuit Count | Total
Ainaloa 11 | 920.8989 | 1722 | x |  |  |  |  | 0 | Total Circuits | 137
Ainaloa 12 | 647.9939 | 1319 | x |  |  |  |  | 0 | Existing HC Satisfies Need | 95
Anaehoomalu 11 | 231.7237 | 1411.1 | x |  |  |  |  | 0 | Updated HC (w/o Modifications) | 21
Anaehoomalu 12 | 394.951 | 2083.4475 | x |  |  |  |  | 0 | Updated HC (w Modifications) | 19
Anaehoomalu 13 | 281.3362 | 4099.1687 | x |  |  |  |  | 0 | Solution Option Required | 2
Captain Cook 11 | 1940.1465 | 3876 | x |  |  |  |  | 0
Captain Cook 12 | 1482.6486 | 1795 | x |  |  |  |  | 0
Hakalau 1 | 213.6153 | 319 | x |  |  |  |  | 0
Halaula 1 | 775.8714 | 743 |  | 1375 |  |  | x | 32.8714 | Hosting Capacity Increase (kW) | 20636.8806
Halaula 2 | 0 | 0 | x |  |  |  |  | 0
Hale Pohaku 11 | 308.28 | 85 |  | 3730 | x |  |  | 223.28
Hale Pohaku 12 | 130.0463 | 83 |  | 2370 | x |  |  | 47.0463
Haleaha 11 | 626.8683 | 2624.657 | x |  |  |  |  | 0
Haleaha 12 | 1944.1977 | 4433 | x |  |  |  |  | 0
Hawaiian Beaches 11 | 989.0585 | 2129 | x |  |  |  |  | 0
Hawaiian Beaches 12 | 7.2911 | 127 | x |  |  |  |  | 0
Hawaiian Paradise Park 11 | 928.4618 | 3346 | x |  |  |  |  | 0
Hawaiian Paradise Park 12 | 1800.8496 | 2819 | x |  |  |  |  | 0
Hawaiian Paradise Park 13 | 4746.5257 | 0 |  | 6156 |  | x |  | 4746.5257
Hawaiian Paradise Park 14 | 806.4122 | 0 |  | 1200 |  | x |  | 806.4122
Hawi 11 | 633.7418 | 1302 | x |  |  |  |  | 0
Hawi 12 | 491.9728 | 1594.1762 | x |  |  |  |  | 0
Honokaa 12 | 736.2424 | 624 |  | 1300 |  | x |  | 112.2424
Honokaa 14 | 985.4316 | 1597 | x |  |  |  |  | 0
Honomu 1 | 288.1686 | 272 |  | 1600 | x |  |  | 16.1686
Host Park 11 | 1250.6584 | 943 |  | 3020 | x |  |  | 307.6584
Host Park 12 | 0 | 0 | x |  |  |  |  | 0
Host Park 13 | 105.4025 | 568 | x |  |  |  |  | 0
Host Park 14 | 662.8252 | 750 | x |  |  |  |  | 0
Huehue 11 | 7287.1127 | 7997 | x |  |  |  |  | 0
Kahaluu 11 | 2586.5058 | 3221 | x |  |  |  |  | 0
Kahaluu 12 | 1375.5427 | 3138.227 | x |  |  |  |  | 0
Kahaluu 14 | 341.2543 | 1183.068 | x |  |  |  |  | 0
Kahaluu 15 | 2221.94 | 1857 |  | 5000 | x |  |  | 364.94
Kailua 11 | 2914.0873 | 6628.674 | x |  |  |  |  | 0
Kailua 12 | 233.0952 | 5558 | x |  |  |  |  | 0
Kailua 15 | 4036.0951 | 8618.3335 | x |  |  |  |  | 0
Kaloko 11 | 1991.538 | 2756 | x |  |  |  |  | 0
Kaloko 12 | 384.4691 | 215 |  | 759 | x |  |  | 169.4691
Kaloko 13 | 1550.7017 | 1818 | x |  |  |  |  | 0
Kaloko 14 | 55.9637 | 242.651 | x |  |  |  |  | 0
Kamuela 11 | 45.6819 | 1935.845 | x |  |  |  |  | 0
Kamuela 12 | 1476.9284 | 2107 | x |  |  |  |  | 0
Kanoelehua 11 | 889.2026 | 1223 | x |  |  |  |  | 0
Kanoelehua 1101 | 957.5372 | 3607 | x |  |  |  |  | 0
Kanoelehua 12 | 768.5352 | 424 |  | 2600 | x |  |  | 344.5352
Kanoelehua 13 | 125.9368 | 81 |  | 1200 | x |  |  | 44.9368
Kanoelehua 14 | 1432.9367 | 2676 | x |  |  |  |  | 0
Kanoelehua 1401 | 1326.4856 | 764 |  | 3000 | x |  |  | 562.4856
Kanoelehua 15 | 1691.9542 | 599 |  | 5000 | x |  |  | 1092.9542
Kanoelehua 17 | 566.8084 | 3891.86 | x |  |  |  |  | 0
Kapua 11 | 1566.4892 | 984.7144 |  | 2170 |  | x |  | 581.7748
Kapua 12 | 875.5895 | 3515.3735 | x |  |  |  |  | 0
Kauhale 11 | 1140.9104 | 864 |  | 2380 |  | x |  | 276.9104
Kauhale 12 | 193.9228 | 0 |  | 2010 |  | x |  | 193.9228
Kaumana 11 | 2855.6633 | 3406 | x |  |  |  |  | 0
Kaumana 12 | 826.1189 | 1425 | x |  |  |  |  | 0
Kawaihae 11 | 265.2693 | 299 | x |  |  |  |  | 0
Kawaihae 12 | 464.5742 | 548 | x |  |  |  |  | 0
Kawaihae 13 | 22.5361 | 62 | x |  |  |  |  | 0
Kawailani 11 | 2457.2549 | 2699 | x |  |  |  |  | 0
Kawailani 12 | 2347.9113 | 2912.812 | x |  |  |  |  | 0
Keahole Airport 11 | 1315.1778 | 1252 |  | 1800 |  | x |  | 63.1778
Keahole Airport 12 | 366.6219 | 427.42 | x |  |  |  |  | 0
Keahole Airport 13 | 835.8372 | 940 | x |  |  |  |  | 0
Keahuolu 11 | 254.619 | 1354 | x |  |  |  |  | 0
Keahuolu 12 | 679.6013 | 2414.4913 | x |  |  |  |  | 0
Kealakehe 11 | 1042.4462 | 1579 | x |  |  |  |  | 0
Kealia 11 | 351.6951 | 898.975 | x |  |  |  |  | 0
Kealia 12 | 589.595 | 804 | x |  |  |  |  | 0
Keauhou 11 | 1293.3842 | 1674 | x |  |  |  |  | 0
Keauhou 13 | 1438.7696 | 2153.9983 | x |  |  |  |  | 0
Komohana 12 | 3831.4162 | 1355 |  | 6395 |  | x |  | 2476.4162
Komohana 13 | 3483.5099 | 6695 | x |  |  |  |  | 0
Komohana 14 | 267.6236 | 851.4 | x |  |  |  |  | 0
Kuakini 11 | 4605.8255 | 4854 | x |  |  |  |  | 0
Kuakini 13 | 1095.2206 | 1019.632 |  | 2038 | x |  |  | 75.5886
Kuakini 14 | 4552.3514 | 4495.5382 |  | 5753 | x |  |  | 56.8131
Kulani 12 | 37.6485 | 120 | x |  |  |  |  | 0
Kurtistown 12 | 1105.4268 | 480 |  | 1800 |  | x |  | 625.4268
Lalamilo 11 | 859.0016 | 1135.9887 | x |  |  |  |  | 0
Lalamilo 12 | 317.6815 | 339.7315 | x |  |  |  |  | 0
Laupahoehoe 1 | 104.9783 | 133 | x |  |  |  |  | 0
Laupahoehoe 2 | 222.2254 | 190 |  | 281 |  | x |  | 32.2254
Maliu Ridge 11 | 405.0684 | 471 | x |  |  |  |  | 0
Maliu Ridge 12 | 505.5593 | 816.0253 | x |  |  |  |  | 0
Mauna Lani 11 | 2878.1914 | 4848.3655 | x |  |  |  |  | 0
Mauna Lani 13 | 1003.0733 | 1701 | x |  |  |  |  | 0
Mauna Lani 14 | 4374.6466 | 2805 |  | 5860 | x |  |  | 1569.6466
Mountain View 11 | 1169.2317 | 2429 | x |  |  |  |  | 0
Mountain View 12 | 305.8467 | 406 | x |  |  |  |  | 0
Namakani Paio | 222.2718 | 128 |  | 1113.4407 |  | x |  | 94.2718
Ookala | 198.5095 | 117 |  | 2370 |  | x |  | 81.5095
Orchid Isle 11 | 71.5719 | 43 |  | 503.5597 |  | x |  | 28.5719
Orchid Isle 12 | 405.8678 | 219 |  | 1268.836 |  | x |  | 186.8678
Ouli 11 | 621.2767 | 3381.4935 | x |  |  |  |  | 0
Ouli 12 | 1168.3647 | 4202 | x |  |  |  |  | 0
Paauilo 1 | 288.9242 | 172 |  | 450 |  | x |  | 116.9242
Pahala 11 | 414.796 | 851 | x |  |  |  |  | 0
Pahala 12 | 82.8001 | 310 | x |  |  |  |  | 0
Palani 11 | 113.0157 | 706.6898 | x |  |  |  |  | 0
Palani 12 | 2398.5935 | 4171 | x |  |  |  |  | 0
Palani 13 | 0 | 0 | x |  |  |  |  | 0
Palani 14 | 817.9263 | 0 |  | 2000 | x |  |  | 817.9263
Panaewa 11 | 1292.5941 | 2107.258 | x |  |  |  |  | 0
Panaewa 12 | 2388.1212 | 1483 |  | 8110 |  | x |  | 905.1212
Papaaloa 1 | 197.7407 | 401 | x |  |  |  |  | 0
Papaaloa 2 | 129.0587 | 460.2552 | x |  |  |  |  | 0
Poopoomino 11 | 1829.9743 | 2055.3263 | x |  |  |  |  | 0
Poopoomino 12 | 936.3586 | 4699.7542 | x |  |  |  |  | 0
Poopoomino 13 | 719.6956 | 2117.175 | x |  |  |  |  | 0
Poopoomino 14 | 1750.3359 | 2830 | x |  |  |  |  | 0
Punaluu 11 | 16.9683 | 1118 | x |  |  |  |  | 0
Punaluu 12 | 187.2866 | 678 | x |  |  |  |  | 0
Puueo 11 | 1496.0456 | 836 |  | 2180 |  | x |  | 660.0456
Puueo 12 | 1537.2004 | 1070 |  | 9080 |  | x |  | 467.2004
Puueo 1402 | 1099.1167 | 4399 | x |  |  |  |  | 0
Puuhuluhulu 11 | 706.9694 | 124 |  | 974 | x |  |  | 582.9694
Puuhuluhulu 12 | 706.9694 | 648 |  | 893.4 | x |  |  | 58.9694
Puukapu 11 | 1473.3492 | 2037 | x |  |  |  |  | 0
Puuwaawaa 11 | 100 | 0 |  | 180 |  |  | x | 100
Puuwaawaa 12 | 286.5751 | 670.1336 | x |  |  |  |  | 0
Royal Hawaiian | 319.7721 | 802 | x |  |  |  |  | 0
Shipman 11 | 401.2744 | 16 |  | 550 | x |  |  | 385.2744
Shipman 12 | 1460.7356 | 1008 |  | 4000 | x |  |  | 452.7356
South Point 11 | 1557.1303 | 1582.338 | x |  |  |  |  | 0
South Point 12 | 56.0618 | 174.042 | x |  |  |  |  | 0
Umauma 11 | 79.6199 | 146 | x |  |  |  |  | 0
Umauma 12 | 137.6555 | 126 |  | 250 | x |  |  | 11.6555
Waika 11 | 118.4827 | 137.0328 | x |  |  |  |  | 0
Waika 12 | 2113.6702 | 2445.83 | x |  |  |  |  | 0
Waikii 11 | 448.0699 | 600.6339 | x |  |  |  |  | 0
Waikii 12 | 211.3683 | 0 |  | 3250 | x |  |  | 211.3683
Waikoloa 11 | 1864.6785 | 3314.9605 | x |  |  |  |  | 0
Waikoloa 12 | 4676.0637 | 4055 |  | 5913 |  | x |  | 621.0637
Waipunahina 11 | 351.0163 | 320.0396 |  | 450 | x |  |  | 30.9768
Wright Road 11 | 999.2303 | 1606 | x |  |  |  |  | 0

## Maui Island HC Results
Return to Assumptions Summary
Maui Island Hosting Capacity Analysis Results by Circuit - Base Forecast
The Hosting Capacity Analysis Results by Circuit shows the Existing Hosting Capacity (HC) rating compared to the Total 2025 DER Forecast. The Total 2025 DER is the total anticipated DER in year 2025. Circuits with existing hosting capacity able to accommodate the Total 2025 DER are marked with an “X” in the Existing HC Satisfies Need column. Circuits with updated hosting capacity able to accommodate the Total 2025 DER without any modifications are marked with an “X” in the Updated HC (w/o Mods) Satisfies Need column. Circuits with updated hosting capacity and modifications (non-infrastructure investment solutions) able to accommodate the Total 2025 DER are marked with an “X” in the Updated HC (w/ Mods) Satisfies Needs column. Circuits that require infrastructure investment solutions are marked with an "X" in the Solution Option Required column. Additional details for these circuits are shown in the Grid Needs Assessment (GNA) tables. The Circuit Count provides a summary of the hosting caapcity results. The Hosting Capacity Increase (kW) is an estimate of the increase in hosting capacity due to the total updated hosting capacity available for all circuits as a result of this analysis. The Total 2025 DER forecast and hosting capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
Circuit Name | Total 2025 DER (kW) | Existing HC (kW) | Existing HC Satisfies Need | Updated HC (kW) | Updated HC (w/o Mods) Satisfies Need | Updated HC (w/ Mods) Satisfies Need | Solution Option Required | HC Increase (kW) | Circuit Count | Total
Haiku 16/1358 | 2605.0897 | 3377.73 | x |  |  |  |  | 0 | Total Circuits | 88
Haiku 16/1361 | 856.232 | 1261.01 | x |  |  |  |  | 0 | Existing HC Satisfies Need | 58
Hana 41/10277 | 91.2729 | 0 |  | 181 | x |  |  | 91.2729 | Updated HC (w/o Modifications) | 15
Hana 41/537 | 146.9528 | 0 |  | 229 | x |  |  | 146.9528 | Updated HC (w Modifications) | 12
Hana 41/6528 | 46.0182 | 0 |  | 116 | x |  |  | 46.0182 | Solution Option Required | 3
Huelo 74A/Huelo | 189.2367 | 192 | x |  |  |  |  | 0
Kahului 8/1264 | 1036.8388 | 3265.9 | x |  |  |  |  | 0
Kahului 8/1265 | 3015.0165 | 3684.7 | x |  |  |  |  | 0
Kahului 8/4048 | 1349.7416 | 1420 | x |  |  |  |  | 0 | Hosting Capacity Increase (kW) | 46995.7451
Kahului 8/4049 | 1147.1297 | 338 |  | 3140 |  | x |  | 809.1297
Kahului 8/4050 | 497.4822 | 955.2 | x |  |  |  |  | 0
Kailua 9/Kailua | 15.8391 | 67.082 | x |  |  |  |  | 0
Kanaha 2/1244 | 1876.7642 | 5049.425 | x |  |  |  |  | 0
Kanaha 2/1245 | 1270.4765 | 1861.619 | x |  |  |  |  | 0
Kanaha 2/1304 | 2058.2794 | 4447.5145 | x |  |  |  |  | 0
Kanaha 2/1305 | 2500.4907 | 3973.427 | x |  |  |  |  | 0
Kanaha 2/1347 | 2516.2598 | 6172.32 | x |  |  |  |  | 0
Kanaha 2/1348 | 910.7414 | 8361.8 | x |  |  |  |  | 0
Kaonoulu/1590 | 4658.1389 | 0 |  | 6000 | x |  |  | 4658.1389
Kaonoulu/1591 | 1260.2853 | 0 |  | 3000 | x |  |  | 1260.2853
Kauhikoa 98/1295 | 986.4812 | 1142.91 | x |  |  |  |  | 0
Keanae 42/Keanae | 34.524 | 173.315 | x |  |  |  |  | 0
Kihei 35/1253 | 1829.0958 | 5087.26 | x |  |  |  |  | 0
Kihei 35/1254 | 4015.7612 | 6100.11 | x |  |  |  |  | 0
Kihei 35/1384 | 8907.8914 | 1158.9 |  | 9900 | x |  |  | 7748.9914
Kihei 35/1385 | 1524.2466 | 1847.3 | x |  |  |  |  | 0
Kihei 35/1473 | 3754.9775 | 0 |  | 5656.5 | x |  |  | 3754.9775
Kihei 35/1515 | 7670.2111 | 7610.25 |  | 7700 |  | x |  | 59.9611
Kuau 73/4066 | 866.9616 | 551.5 |  | 1940 |  | x |  | 315.4616
Kuihelani 209/1653 | 5161.0114 | 0 |  | 7019.36 |  | x |  | 5161.0114
Kuihelani 209/1708 | 2955.3508 | 0 |  | 4260 |  | x |  | 2955.3508
Kula 13/1237 | 3292.579 | 2658.6 |  | 4500 |  |  | x | 633.979
Kula 13/1238 | 3347.827 | 3227 |  | 5500 |  | x |  | 120.827
Kula Ag Park 55/1322 | 811.8405 | 448.53 |  | 1252 | x |  |  | 363.3105
Lahaina 34/1221 | 2434.8854 | 4090 | x |  |  |  |  | 0
Lahaina 34/1223 | 6249.2417 | 3078.11 |  | 6876.6 | x |  |  | 3171.1317
Lahaina 34/1225 | 681.1939 | 2139.26 | x |  |  |  |  | 0
Lahaina 34/1226 | 381.2637 | 1485 | x |  |  |  |  | 0
Lahaina 34/1390 | 3052.2012 | 0 |  | 4000 | x |  |  | 3052.2012
Lahaina 34/1397 | 238.1146 | 1797.4 | x |  |  |  |  | 0
Lahaina 34/1398 | 5078.7723 | 971.6 |  | 7000 |  |  | x | 4107.1723
Maalaea 39/1285 | 970.4456 | 4212.3 | x |  |  |  |  | 0
Maalaea 39/1286 | 1311.3755 | 2420.01 | x |  |  |  |  | 0
Mahinahina 50/1219 | 2710.6467 | 12477.51 | x |  |  |  |  | 0
Mahinahina 50/1380 | 832.0918 | 1283.48 | x |  |  |  |  | 0
Mahinahina 50/1381 | 3824.7302 | 5289 | x |  |  |  |  | 0
Makawao 12/1234 | 976.3382 | 1385.4 | x |  |  |  |  | 0
Makawao 12/1235 | 1623.012 | 1536.8 |  | 2474.1925 | x |  |  | 86.212
Makawao 12/1236 | 1312.6938 | 1315.9 | x |  |  |  |  | 0
Maui Hardwoods 75/522 | 485.4909 | 1503.7 | x |  |  |  |  | 0
Napili 29/1232 | 596.3956 | 4997.55 | x |  |  |  |  | 0
Napili 29/1420 | 3170.6182 | 2453.72 |  | 4252 | x |  |  | 716.8982
Napili 29/1421 | 1121.9551 | 1592.6 | x |  |  |  |  | 0
Onehee 40/4055 | 1480.0223 | 1700 | x |  |  |  |  | 0
Onehee 40/4056 | 606.9957 | 743.38 | x |  |  |  |  | 0
Paia Mauka 93/4042 | 1466.1585 | 521.5 |  | 1680 |  |  | x | 944.6585
Peahi 94/1294 | 1798.2829 | 1456.7 |  | 2430 |  | x |  | 341.5829
Pukalani 17/1282 | 3533.4107 | 2927.3 |  | 5983.29 |  | x |  | 606.1107
Pukalani 17/1283 | 7.8293 | 1060.14 | x |  |  |  |  | 0
Pukalani 17/1308 | 4931.9475 | 5155.9 | x |  |  |  |  | 0
Pukalani 17/1309 | 523.3023 | 1314.71 | x |  |  |  |  | 0
Puukolii 23/1270 | 6395.9574 | 14132.5 | x |  |  |  |  | 0
Puukolii 23/1271 | 1327.2114 | 4445.9 | x |  |  |  |  | 0
Puukolii 23/1272 | 3583.9692 | 5865.4 | x |  |  |  |  | 0
Puukolii 23/1273 | 123.3704 | 730.72 | x |  |  |  |  | 0
Spreckelsville 92/4043 | 1211.0952 | 0 |  | 1470 |  | x |  | 1211.0952
Waiehu 43/1378 | 2550.8913 | 3261.42 | x |  |  |  |  | 0
Waiehu 43/1379 | 4210.8283 | 3922.55 |  | 5000 | x |  |  | 288.2783
Waiinu 36/1266 | 1262.0155 | 3822.12 | x |  |  |  |  | 0
Waiinu 36/1267 | 677.2238 | 1759.85 | x |  |  |  |  | 0
Waiinu 36/1492 | 1148.9552 | 3484.74 | x |  |  |  |  | 0
Waiinu 36/1493 | 9404.6979 | 8021.54 |  | 12000 |  | x |  | 1383.1579
Waiinu 36/2030 | 361.7556 | 848.9 | x |  |  |  |  | 0
Waikapu 77/524 | 0 | 826.914 | x |  |  |  |  | 0
Wailea 25/1280 | 3213.8775 | 4155.22 | x |  |  |  |  | 0
Wailea 25/1281 | 791.2489 | 3060.13 | x |  |  |  |  | 0
Wailea 25/1320 | 2804.7905 | 6017.472 | x |  |  |  |  | 0
Wailea 25/1321 | 35.9539 | 3997.46 | x |  |  |  |  | 0
Wailea 25/1395 | 551.3852 | 4018.53 | x |  |  |  |  | 0
Wailea 25/1396 | 1017.8138 | 3574.2 | x |  |  |  |  | 0
Wailea 25/1517 | 3136.4295 | 2705.41 |  | 3500 |  | x |  | 431.0195
Wailea 25/1518 | 1898.7447 | 1632.631 |  | 4000 |  | x |  | 266.1137
Wailuku 3/1290 | 5064.0886 | 3242.2 |  | 6004.23 | x |  |  | 1821.8886
Wailuku 3/1447 | 3418.9568 | 5574.3 | x |  |  |  |  | 0
Wailuku 3/4031 | 649.3283 | 1079.01 | x |  |  |  |  | 0
Wailuku 3/4037 | 1015.7662 | 573.21 |  | 1300 | x |  |  | 442.5562
Wailuku Heights 18/493 | 997.724 | 1300 | x |  |  |  |  | 0
Wailuku Heights 18/529 | 650.4925 | 1400 | x |  |  |  |  | 0

## Lanai HC Results
Return to Assumptions Summary
Lana‘i Hosting Capacity Analysis Results by Circuit - Base Forecast
The Hosting Capacity Analysis Results by Circuit shows the Existing Hosting Capacity (HC) rating compared to the Total 2025 DER Forecast. The Total 2025 DER is the total anticipated DER in year 2025. Circuits with existing hosting capacity able to accommodate the Total 2025 DER are marked with an “X” in the Existing HC Satisfies Need column. Circuits with updated hosting capacity able to accommodate the Total 2025 DER without any modifications are marked with an “X” in the Updated HC (w/o Mods) Satisfies Need column. Circuits with updated hosting capacity and modifications (non-infrastructure investment solutions) able to accommodate the Total 2025 DER are marked with an “X” in the Updated HC (w/ Mods) Satisfies Needs column. Circuits that require infrastructure investment solutions are marked with an "X" in the Solution Option Required column. Additional details for these circuits are shown in the Grid Needs Assessment (GNA) tables. The Circuit Count provides a summary of the hosting caapcity results. The Hosting Capacity Increase (kW) is an estimate of the increase in hosting capacity due to the total updated hosting capacity available for all circuits as a result of this analysis. The Total 2025 DER forecast and hosting capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
Circuit Name | Total 2025 DER (kW) | Existing HC (kW) | Existing HC Satisfies Need | Updated HC (kW) | Updated HC (w/o Mods) Satisfies Need | Updated HC (w/ Mods) Satisfies Need | Solution Option Required | HC Increase (kW) | Circuit Count | Total
Miki Basin PP 302/1208 | 408.2167 | 386 |  | 2700 |  |  | x | 22.2167 | Total Circuits | 3
Miki Basin PP 302/1210 | 2170.5203 | 2154 |  | 3900 |  |  | x | 16.5203 | Existing HC Satisfies Need | 1
Miki Basin PP 302/1212 | 471.902 | 2664.3 | x |  |  |  |  | 0 | Updated HC (w/o Modifications) | 0
[9 empty] | Updated HC (w Modifications) | 0
[9 empty] | Solution Option Required | 2
[9 empty] | Hosting Capacity Increase (kW) | 38.737

## Molokai HC Results
Return to Assumptions Summary
Moloka‘i Hosting Capacity Analysis Results by Circuit - Base Forecast
The Hosting Capacity Analysis Results by Circuit shows the Existing Hosting Capacity (HC) rating compared to the Total 2025 DER Forecast. The Total 2025 DER is the total anticipated DER in year 2025. Circuits with existing hosting capacity able to accommodate the Total 2025 DER are marked with an “X” in the Existing HC Satisfies Need column. Circuits with updated hosting capacity able to accommodate the Total 2025 DER without any modifications are marked with an “X” in the Updated HC (w/o Mods) Satisfies Need column. Circuits with updated hosting capacity and modifications (non-infrastructure investment solutions) able to accommodate the Total 2025 DER are marked with an “X” in the Updated HC (w/ Mods) Satisfies Needs column. Circuits that require infrastructure investment solutions are marked with an "X" in the Solution Option Required column. Additional details for these circuits are shown in the Grid Needs Assessment (GNA) tables. The Circuit Count provides a summary of the hosting caapcity results. The Hosting Capacity Increase (kW) is an estimate of the increase in hosting capacity due to the total updated hosting capacity available for all circuits as a result of this analysis. The Total 2025 DER forecast and hosting capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
Circuit Name | Total 2025 DER (kW) | Existing HC (kW) | Existing HC Satisfies Need | Updated HC (kW) | Updated HC (w/o Mods) Satisfies Need | Updated HC (w/ Mods) Satisfies Need | Solution Option Required | HC Increase (kW) | Circuit Count | Total
Palaau PP 81/105A | 993.031 | 1025.5 | x |  |  |  |  | 0 | Total Circuits | 8
Palaau PP 81/106B | 263.7536 | 282.2 | x |  |  |  |  | 0 | Existing HC Satisfies Need | 5
Palaau PP 81/109B | 134.7726 | 125 |  | 800 |  |  | x | 9.7726 | Updated HC (w/o Modifications) | 0
Palaau PP 81/110B | 267.7232 | 212 |  | 1000 |  |  | x | 55.7232 | Updated HC (w Modifications) | 0
Palaau PP 81/111A | 1308.6298 | 823 |  | 2050 |  |  | x | 485.6298 | Solution Option Required | 3
Puunana 80/1466 | 40.881 | 1061 | x |  |  |  |  | 0
Puunana 80/1467 | 199.5484 | 613 | x |  |  |  |  | 0
Puunana 80/1468 | 11.6074 | 532 | x |  |  |  |  | 0
[9 empty] | Hosting Capacity Increase (kW) | 551.1256

## Oahu Total DER
Return to Assumptions Summary
O‘ahu Total Anticipated DER and Hosting Capacity by Circuit (kW) - Base Forecast
The Total Anticipated DER is the sum of the Executed DER and the Adjusted DER Growth by Circuit. The Executed DER for each circuit is the aggregated program size (kW) of all executed DER programs on that circuit as of December 31, 2020. The Hosting Capacity (HC) by circuit is provided for comparison. The Existing HC is the current hosting capacity for each circuit. The Updated HC is the updated hosting capacity as a result of this analysis. The Executed DER, Total Anticipated DER, and Hosting Capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
|  | Total Anticipated DER |  |  |  |  | Hosting Capacity
Circuit | Executed DER | 2021 | 2022 | 2023 | 2024 | 2025 | Existing HC | Updated HC
AHUA | 959.7 | 1087.476 | 1400.608 | 1604.482 | 1706.419 | 1810.073 | 1561 | 5210
AIEA | 2895.347 | 3120.907 | 3275.993 | 3455.377 | 3824.475 | 3896.209 | 3601 | 5700
AINA KOA | 1887.727 | 2271.595 | 2648.807 | 3288.381 | 3368.11 | 3512.682 | 2951 | 4080
ANOI | 3761.365 | 3956.278 | 4223.632 | 4369.927 | 4427.986 | 4479.363 | 3794 | 5140
ANUU | 3028.055 | 3096.148 | 3465.556 | 3552.987 | 3752.331 | 4152.953 | 4073 | 4690
CKT 16 | 2214.53 | 6588.53 | 7189.928 | 7291.326 | 7491.326 | 7591.326 | 6611 | 10012
DIAMOND HEAD | 290.68 | 712.725 | 997.234 | 1438.713 | 1857.933 | 1985.33 | 1452 | 3280
EWA BEACH 4 | 4230.719 | 4485.378 | 5343.485 | 5664.24 | 5788.231 | 5969.706 | 5966 | 8046
EWA NUI 2 | 3539.612 | 4244.902 | 4713.828 | 5165.499 | 5662.265 | 6239.402 | 6024 | 8089
HAUULA | 1534.12 | 6500.617 | 6599.836 | 6716.247 | 6779.436 | 6833.55 | 2802 | 9310.9
HEIGHTS | 1026.56 | 1062.551 | 1134.708 | 1183.428 | 1206.965 | 1226.635 | 1145 | 1397.5
HILA 4 | 400 | 400 | 400 | 400 | 400 | 400 | 0 | 2323
HOAEAE 3 | 1134.32 | 1756.837 | 2118.316 | 2393.706 | 2498.412 | 2681.819 | 2488 | 4038
KAHALA 3 | 1013.192 | 5040.282 | 5606.95 | 6094.137 | 6164.436 | 6315.024 | 1609 | 7269
KAHUKU | 1453.58 | 1620.961 | 1818.877 | 2327.834 | 2360.647 | 2704.787 | 2422 | 3510
KAINALU | 1452.85 | 1597.979 | 1761.183 | 2027.46 | 2159.01 | 2199.462 | 1047 | 2300
KALOI 1 | 714.56 | 814.56 | 1014.56 | 1114.56 | 1114.56 | 1114.56 | 612 | 2979
KAPOLEI 4 | 1288.9 | 6415.252 | 6594.495 | 6661.15 | 6688.314 | 6733.895 | 2966 | 6971
KAWAILOA | 1109.9 | 1200.413 | 1297.143 | 1392.444 | 1430.992 | 1458.5 | 1133 | 2467.46
KEWALO | 2008.74 | 2125.991 | 2300.036 | 2465.877 | 7201.511 | 7285.366 | 7024 | 11693
KILAUEA 4KV | 869.41 | 894.591 | 951.995 | 983.721 | 1002.783 | 1011.748 | 962 | 1300
MAKAKILO 2 | 4656.717 | 5025.13 | 8379.205 | 8991.779 | 9104.334 | 9312.231 | 8472 | 10570
MANOA-PIIKOI | 963.705 | 1148.02 | 1481.154 | 1573.093 | 1831.391 | 1872.599 | 1553 | 2090
MAPUNAPUNA | 228.27 | 437.243 | 550.673 | 550.673 | 650.673 | 750.673 | 371 | 3631
MAUKA | 6030.66 | 6619.175 | 8343.409 | 9074.746 | 9390.555 | 10010.065 | 8350 | 10283
MIKILUA 3 | 3777.53 | 4193.552 | 4527.89 | 4695.288 | 5068.128 | 5152.28 | 4761 | 5440
MIKILUA 4 | 5016.675 | 5196.348 | 5811.095 | 6007.537 | 6172.71 | 6244.546 | 3514 | 7653
OCEAN POINTE 4 | 1094.63 | 1145.015 | 1230.011 | 1319.951 | 1369.159 | 1401.258 | 1362 | 1713
ONEAWA | 804.874 | 829.703 | 866.559 | 900.393 | 915.771 | 935.925 | 908 | 1860
PAHIA | 1073.18 | 1552.592 | 1802.607 | 1998.421 | 2045.57 | 2090.522 | 1505 | 4730
PIIKOI 8 | 1457.95 | 1671.871 | 1952.745 | 2172.525 | 2228.412 | 2368.024 | 1993 | 3469
WAIALUA | 1335.065 | 1721.453 | 1951.776 | 2232.387 | 2383.788 | 2438.891 | 1711 | 3301.66
WAIHEE 3 | 395.21 | 406.43 | 549.783 | 623.019 | 694.47 | 709.425 | 660 | 1120
WILIWILI 2 | 1947.807 | 1994.342 | 2063.878 | 2140.034 | 2176.027 | 2219.018 | 2126 | 2566

## Hawaii Island Total DER
Return to Assumptions Summary
Hawai‘i Island Total Anticipated DER and Hosting Capacity by Circuit (kW) - Base Forecast
The Total Anticipated DER is the sum of the Executed DER and the Adjusted DER Growth by Circuit. The Executed DER for each circuit is the aggregated program size (kW) of all executed DER programs on that circuit as of December 31, 2020. The Hosting Capacity (HC) by circuit is provided for comparison. The Existing HC is the current hosting capacity for each circuit. The Updated HC is the updated hosting capacity as a result of this analysis. The Executed DER, Total Anticipated DER, and Hosting Capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
|  | Total Anticipated DER |  |  |  |  | Hosting Capacity
Circuit | Executed DER | 2021 | 2022 | 2023 | 2024 | 2025 | Existing HC | Updated HC
Halaula 1 | 585.276 | 635.1896 | 674.3269 | 716.4603 | 744.9073 | 775.8714 | 743 | 1375
Hale Pohaku 11 | 232.55 | 252.3823 | 267.933 | 284.674 | 295.9769 | 308.28 | 85 | 3730
Hale Pohaku 12 | 98.1 | 106.4662 | 113.0261 | 120.0882 | 124.8563 | 130.0463 | 83 | 2370
Hawaiian Paradise Park 13 | 3580.5257 | 3885.8804 | 4125.3101 | 4383.0678 | 4557.0972 | 4746.5257 | 0 | 6156
Hawaiian Paradise Park 14 | 608.3143 | 660.1927 | 700.8706 | 744.6625 | 774.2292 | 806.4122 | 0 | 1200
Honokaa 12 | 555.382 | 602.7461 | 639.8845 | 679.8658 | 706.8598 | 736.2424 | 624 | 1300
Honomu 1 | 217.379 | 235.9175 | 250.4537 | 266.1025 | 276.6681 | 288.1686 | 272 | 1600
Host Park 11 | 943.43 | 1023.8877 | 1086.9748 | 1154.8912 | 1200.7461 | 1250.6584 | 943 | 3020
Kahaluu 15 | 1676.113 | 1819.0554 | 1931.137 | 2051.7984 | 2133.2649 | 2221.94 | 1857 | 5000
Kaloko 12 | 290.023 | 314.7568 | 334.1506 | 355.029 | 369.1254 | 384.4691 | 215 | 759
Kanoelehua 12 | 584.655 | 632.81 | 670.5684 | 711.2173 | 738.662 | 768.5352 | 424 | 2600
Kanoelehua 13 | 95 | 103.1018 | 109.4544 | 116.2934 | 120.9108 | 125.9368 | 81 | 1200
Kanoelehua 1401 | 1000.63 | 1085.9658 | 1152.8779 | 1224.9121 | 1273.5471 | 1326.4856 | 764 | 3000
Kanoelehua 15 | 1276.32 | 1385.1672 | 1470.5147 | 1562.3955 | 1624.4303 | 1691.9542 | 599 | 5000
Kapua 11 | 1486.286 | 1507.2898 | 1523.7589 | 1541.4888 | 1553.4593 | 1566.4892 | 984.7144 | 2170
Kauhale 11 | 865.555 | 937.6657 | 994.2079 | 1055.0784 | 1096.1761 | 1140.9104 | 864 | 2380
Kauhale 12 | 146.285 | 158.7605 | 168.5426 | 179.0734 | 186.1835 | 193.9228 | 0 | 2010
Keahole Airport 11 | 992.1 | 1076.7084 | 1143.0501 | 1214.4701 | 1262.6906 | 1315.1778 | 1252 | 1800
Komohana 12 | 2890.216 | 3136.6997 | 3329.9683 | 3538.0315 | 3678.5088 | 3831.4162 | 1355 | 6395
Kuakini 13 | 826.176 | 896.634 | 951.8804 | 1011.3558 | 1051.5116 | 1095.2206 | 1019.632 | 2038
Kuakini 14 | 3434.051 | 3726.914 | 3956.5489 | 4203.7621 | 4370.6722 | 4552.3514 | 4495.5382 | 5753
Kurtistown 12 | 833.875 | 904.9896 | 960.7508 | 1020.7805 | 1061.3105 | 1105.4268 | 480 | 1800
Laupahoehoe 2 | 167.635 | 181.9313 | 193.141 | 205.2089 | 213.3567 | 222.2254 | 190 | 281
Mauna Lani 14 | 3300 | 3581.4309 | 3802.1018 | 4039.6648 | 4200.0594 | 4374.6466 | 2805 | 5860
Namakani Paio | 167.67 | 181.9692 | 193.1813 | 205.2517 | 213.4012 | 222.2718 | 128 | 1113.4407
Ookala | 149.745 | 162.5156 | 172.529 | 183.309 | 190.5872 | 198.5095 | 117 | 2370
Orchid Isle 11 | 53.99 | 58.5944 | 62.2047 | 66.0914 | 68.7155 | 71.5719 | 43 | 503.5597
Orchid Isle 12 | 306.165 | 332.2754 | 352.7486 | 374.7891 | 389.6701 | 405.8678 | 219 | 1268.836
Paauilo 1 | 217.949 | 236.5361 | 251.1104 | 266.8003 | 277.3936 | 288.9242 | 172 | 450
Palani 14 | 617 | 669.619 | 710.8778 | 755.2949 | 785.2838 | 817.9263 | 0 | 2000
Panaewa 12 | 1824.71 | 1972.2574 | 2087.9498 | 2212.4983 | 2296.5893 | 2388.1212 | 1483 | 8110
Puueo 11 | 1128.537 | 1224.781 | 1300.2462 | 1381.4883 | 1436.3401 | 1496.0456 | 836 | 2180
Puueo 12 | 1159.582 | 1258.4736 | 1336.0148 | 1419.4917 | 1475.8525 | 1537.2004 | 1070 | 9080
Puuhuluhulu 11 | 533.3 | 578.7809 | 614.4427 | 652.8343 | 678.7551 | 706.9694 | 124 | 974
Puuhuluhulu 12 | 533.3 | 578.7809 | 614.4427 | 652.8343 | 678.7551 | 706.9694 | 648 | 893.4
Puuwaawaa 11 | 0 | 100 | 100 | 100 | 100 | 100 | 0 | 180
Shipman 11 | 302.7 | 328.5149 | 348.7564 | 370.5474 | 385.26 | 401.2744 | 16 | 550
Shipman 12 | 1101.901 | 1195.8734 | 1269.5575 | 1348.882 | 1402.4393 | 1460.7356 | 1008 | 4000
Umauma 12 | 103.84 | 112.6957 | 119.6395 | 127.1148 | 132.1619 | 137.6555 | 126 | 250
Waikii 12 | 159.445 | 173.0428 | 183.7049 | 195.1831 | 202.9329 | 211.3683 | 0 | 3250
Waikoloa 12 | 3527.373 | 3828.1947 | 4064.0701 | 4318.0014 | 4489.4473 | 4676.0637 | 4055 | 5913
Waipunahina 11 | 264.788 | 287.3697 | 305.076 | 324.1378 | 337.0077 | 351.0163 | 320.0396 | 450

## Maui Total DER
Return to Assumptions Summary
Maui Island Total Anticipated DER and Hosting Capacity by Circuit (kW) - Base Forecast
The Total Anticipated DER is the sum of the Executed DER and the Adjusted DER Growth by Circuit. The Executed DER for each circuit is the aggregated program size (kW) of all executed DER programs on that circuit as of December 31, 2020. The Hosting Capacity (HC) by circuit is provided for comparison. The Existing HC is the current hosting capacity for each circuit. The Updated HC is the updated hosting capacity as a result of this analysis. The Executed DER, Total Anticipated DER, and Hosting Capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
|  | Total Anticipated DER |  |  |  |  | Hosting Capacity
Circuit | Executed DER | 2021 | 2022 | 2023 | 2024 | 2025 | Existing HC | Updated HC
Hana 41/10277 | 65.75 | 72.1499 | 77.9698 | 83.5781 | 87.4059 | 91.2729 | 0 | 181
Hana 41/537 | 105.86 | 116.164 | 125.5344 | 134.564 | 140.7268 | 146.9528 | 0 | 229
Hana 41/6528 | 33.15 | 36.3767 | 39.311 | 42.1386 | 44.0685 | 46.0182 | 0 | 116
Kahului 8/4049 | 826.355 | 906.7892 | 979.9357 | 1050.4216 | 1098.5292 | 1147.1297 | 338 | 3140
Kaonoulu/1590 | 3355.572 | 3682.1904 | 3979.2156 | 4265.4369 | 4460.787 | 4658.1389 | 0 | 6000
Kaonoulu/1591 | 907.8686 | 996.2371 | 1076.5989 | 1154.0377 | 1206.8907 | 1260.2853 | 0 | 3000
Kihei 35/1384 | 7428.666 | 7799.5815 | 8136.8903 | 8461.9299 | 8683.7741 | 8907.8914 | 1158.9 | 9900
Kihei 35/1473 | 2704.9639 | 2968.2546 | 3207.6899 | 3438.4161 | 3595.89 | 3754.9775 | 0 | 5656.5
Kihei 35/1515 | 5525.371 | 6063.1892 | 6552.2786 | 7023.578 | 7345.2465 | 7670.2111 | 7610.25 | 7700
Kuau 73/4066 | 624.531 | 685.3204 | 740.6021 | 793.8729 | 830.231 | 866.9616 | 551.5 | 1940
Kuihelani 209/1653 | 3717.825 | 4079.7037 | 4408.7945 | 4725.915 | 4942.3543 | 5161.0114 | 0 | 7019.36
Kuihelani 209/1708 | 2268.755 | 2440.9188 | 2597.4837 | 2748.3538 | 2851.3247 | 2955.3508 | 0 | 4260
Kula 13/1237 | 2371.867 | 2602.7354 | 2812.686 | 3014.9999 | 3153.082 | 3292.579 | 2658.6 | 4500
Kula 13/1238 | 2419.764 | 2652.4756 | 2864.1025 | 3068.0317 | 3207.2162 | 3347.827 | 3227 | 5500
Kula Ag Park 55/1322 | 640.75 | 683.6509 | 722.6648 | 760.2596 | 785.9186 | 811.8405 | 448.53 | 1252
Lahaina 34/1223 | 5304.296 | 5541.241 | 5756.7176 | 5964.3565 | 6106.073 | 6249.2417 | 3078.11 | 6876.6
Lahaina 34/1390 | 2203.74 | 2416.4915 | 2609.9667 | 2796.4045 | 2923.6509 | 3052.2012 | 0 | 4000
Lahaina 34/1398 | 3868.307 | 4171.8309 | 4447.8542 | 4713.8375 | 4895.3748 | 5078.7723 | 971.6 | 7000
Makawao 12/1235 | 1211.11 | 1314.3943 | 1408.3206 | 1498.8305 | 1560.6047 | 1623.012 | 1536.8 | 2474.1925
Napili 29/1420 | 1883.551 | 2768.2205 | 2890.6883 | 3008.7015 | 3089.2472 | 3170.6182 | 2453.72 | 4252
Paia Mauka 93/4042 | 1056.173 | 1158.9768 | 1252.4661 | 1342.5548 | 1404.0417 | 1466.1585 | 521.5 | 1680
Peahi 94/1294 | 1428.25 | 1521.0357 | 1605.4145 | 1686.7242 | 1742.2192 | 1798.2829 | 1456.7 | 2430
Pukalani 17/1282 | 2550.947 | 2797.2996 | 3021.3315 | 3237.2145 | 3384.5577 | 3533.4107 | 2927.3 | 5983.29
Spreckelsville 92/4043 | 875.23 | 959.4481 | 1036.0357 | 1109.8375 | 1160.2083 | 1211.0952 | 0 | 1470
Waiehu 43/1379 | 3033.344 | 3328.598 | 3597.1005 | 3855.8367 | 4032.4278 | 4210.8283 | 3922.55 | 5000
Waiinu 36/1493 | 6774.839 | 7434.2756 | 8033.9642 | 8611.8399 | 9006.2482 | 9404.6979 | 8021.54 | 12000
Wailea 25/1517 | 2259.382 | 2479.3015 | 2679.2953 | 2872.0145 | 3003.5481 | 3136.4295 | 2705.41 | 3500
Wailea 25/1518 | 1367.794 | 1500.9298 | 1622.0028 | 1738.672 | 1818.3004 | 1898.7447 | 1632.631 | 4000
Wailuku 3/1290 | 3648.005 | 4003.0877 | 4325.9982 | 4637.1633 | 4849.5379 | 5064.0886 | 3242.2 | 6004.23
Wailuku 3/4037 | 731.725 | 802.9483 | 867.7184 | 930.1326 | 972.7312 | 1015.7662 | 573.21 | 1300

## Lanai Total DER
Return to Assumptions Summary
Lana‘i Total Anticipated DER and Hosting Capacity by Circuit (kW) - Base Forecast
The Total Anticipated DER is the sum of the Executed DER and the Adjusted DER Growth by Circuit. The Executed DER for each circuit is the aggregated program size (kW) of all executed DER programs on that circuit as of December 31, 2020. The Hosting Capacity (HC) by circuit is provided for comparison. The Existing HC is the current hosting capacity for each circuit. The Updated HC is the updated hosting capacity as a result of this analysis. The Executed DER, Total Anticipated DER, and Hosting Capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
|  | Total Anticipated DER |  |  |  |  | Hosting Capacity
Circuit | Executed DER | 2021 | 2022 | 2023 | 2024 | 2025 | Existing HC | Updated HC
Miki Basin PP 302/1208 | 321.425 | 335.8236 | 348.6224 | 390.6184 | 398.6177 | 408.2167 | 386 | 2700
Miki Basin PP 302/1210 | 2140.644 | 2145.6004 | 2150.0062 | 2164.4624 | 2167.216 | 2170.5203 | 2154 | 3900

## Molokai Total DER
Return to Assumptions Summary
Moloka‘i Total Anticipated DER and Hosting Capacity by Circuit (kW) - Base Forecast
The Total Anticipated DER is the sum of the Executed DER and the Adjusted DER Growth by Circuit. The Executed DER for each circuit is the aggregated program size (kW) of all executed DER programs on that circuit as of December 31, 2020. The Hosting Capacity (HC) by circuit is provided for comparison. The Existing HC is the current hosting capacity for each circuit. The Updated HC is the updated hosting capacity as a result of this analysis. The Executed DER, Total Anticipated DER, and Hosting Capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
|  | Total Anticipated DER |  |  |  |  | Hosting Capacity
Circuit | Executed DER | 2021 | 2022 | 2023 | 2024 | 2025 | Existing HC | Updated HC
Palaau PP 81/109B | 111 | 118.1955 | 122.7497 | 130.2184 | 132.5866 | 134.7726 | 125 | 800
Palaau PP 81/110B | 221.84 | 235.728 | 244.5179 | 258.9333 | 263.5041 | 267.7232 | 212 | 1000
Palaau PP 81/111A | 872.427 | 1178.7872 | 1214.4583 | 1272.9588 | 1291.5077 | 1308.6298 | 823 | 2050

## Summary GNA
Return to Assumptions Summary
Grid Needs Assessment Summary - Base Forecast
These tables summarize the Grid Needs Assessment results for all islands. Non-Infrastrucutre Investments indicate circuits where the solution is a modification to existing equipment (e.g. LTC settings change only). Infrastructure Investments indicate circuits where the solution requires infrastructure investments (e.g. circuit phase balancing, new line voltage regulator, etc).
Island | Total Circuits | Violation Type |  | Solution Option
|  | Voltage | Conductor Overload | Non-Infrastructure Investments | Infrastructure Investments
O‘ahu | 12 | 11 | 1 | 6 | 6
Hawai‘i Island | 21 | 21 | - | 19 | 2
Maui Island | 15 | 15 | 1 | 12 | 3
Lana‘i | 2 | 2 | - | - | 2
Moloka‘i | 3 | 3 | - | - | 3
Total (All Islands) | 53 | 52 | 2 | 37 | 16

## Oahu GNA
Return to Assumptions Summary
O‘ahu Grid Needs Assessment - Base Forecast
The Grid Needs Assessment shows the grid needs identified for each circuit for the next 5 years (years 2021 through 2025). The Violation Type indicates whether a thermal and/or voltage violation triggers the grid need. The Operating Date indicates the date at which traditional infrastructure must be constructed and energized, in advance of the forecasted grid need to maintain safety and reliability. The Traditional Solution lists the solution identified for mitigation. The Cost Estimate is the estimated cost (dollars) to provide traditional solution identified.
Substation | Circuit | Violation Type | Operating Date | Traditional Solution | Cost Estimate
AIEA 2 | AIEA | Voltage | 2024 | LTC setting change | -
WAILUPE | AINA KOA | Voltage | 2023 | Circuit phase balancing | 7200
KAPAHULU 4 | DIAMOND HEAD | Voltage | 2024 | LTC setting change | -
KALAMA 1 4KV | KAINALU | Voltage | 2021 | Dynamic LTC, Install two 1ph line regulators | 294000
WAIALUA 3 | KAWAILOA | Voltage | 2021 | LTC setting change | -
KAHALA 2 4KV | KILAUEA 4KV | Voltage | 2023 | Circuit phase balancing and Install 3ph line regulator | 213600
MAKAKILO 2 | MAKAKILO 2 | Voltage | 2023 | LTC setting change | -
PIIKOI 3 | MANOA-PIIKOI | Voltage | 2023 | Circuit phase balancing and LTC setting change | 3600
MAKAHA 2 | MAUKA | Voltage | 2023 | Circuit phase balancing | 3600
KALAMA 1 4KV | ONEAWA | Voltage | 2024 | LTC setting change | -
PIIKOI 4 | PIIKOI 8 | Conductor overloading | 2023 | Reconductoring | 270000
WAIALUA 3 | WAIALUA | Voltage | 2021 | LTC setting change | -

## Hawaii Island GNA
Return to Assumptions Summary
Hawai‘i Island Grid Needs Assessment - Base Forecast
The Grid Needs Assessment shows the grid needs identified for each circuit for the next 5 years (years 2021 through 2025). The Violation Type indicates whether a thermal and/or voltage violation triggers the grid need. The Operating Date indicates the date at which traditional infrastructure must be constructed and energized, in advance of the forecasted grid need to maintain safety and reliability. The Traditional Solution lists the solution identified for mitigation. The Cost Estimate is the estimated cost (dollars) to provide traditional solution identified.
Substation | Circuit | Violation Type | Operating Date | Traditional Solution | Cost Estimate
Halaula | Halaula 1 | Voltage | 2024 | Install two 3ph line regulator | 420000
Hawaiian Paradise Park 2 | Hawaiian Paradise Park 13 | Voltage | 2021 | LTC setting change | -
Hawaiian Paradise Park 2 | Hawaiian Paradise Park 14 | Voltage | 2021 | LTC setting change | -
Honokaa 2 | Honokaa 12 | Voltage | 2022 | LTC setting change | -
Kapua 1 | Kapua 11 | Voltage | 2021 | LTC setting change | -
Kauhale | Kauhale 11 | Voltage | 2021 | LTC setting change | -
Kauhale | Kauhale 12 | Voltage | 2021 | LTC setting change | -
Keahole Airport | Keahole Airport 11 | Voltage | 2024 | LTC setting change | -
Komohana 1 | Komohana 12 | Voltage | 2021 | LTC setting change | -
Kurtistown | Kurtistown 12 | Voltage | 2021 | LTC setting change | -
Laupahoehoe | Laupahoehoe 2 | Voltage | 2022 | LTC setting change | -
Namakani Paio | Namakani Paio | Voltage | 2021 | LTC setting change | -
Ookala | Ookala | Voltage | 2021 | LTC setting change | -
Orchid Isle | Orchid Isle 11 | Voltage | 2021 | LTC setting change | -
Orchid Isle | Orchid Isle 12 | Voltage | 2021 | LTC setting change | -
Paauilo | Paauilo 1 | Voltage | 2021 | LTC setting change | -
Panaewa | Panaewa 12 | Voltage | 2021 | LTC setting change | -
Puueo 2 | Puueo 11 | Voltage | 2021 | LTC setting change | -
Puueo 2 | Puueo 12 | Voltage | 2021 | LTC setting change | -
Puuwaawaa | Puuwaawaa 11 | Voltage | 2021 | Install 3ph line regulator | 210000
Waikoloa | Waikoloa 12 | Voltage | 2022 | LTC setting change | -

## Maui GNA
Return to Assumptions Summary
Maui Island Grid Needs Assessment - Base Forecast
The Grid Needs Assessment shows the grid needs identified for each circuit for the next 5 years (years 2021 through 2025). The Violation Type indicates whether a thermal and/or voltage violation triggers the grid need. The Operating Date indicates the date at which traditional infrastructure must be constructed and energized, in advance of the forecasted grid need to maintain safety and reliability. The Traditional Solution lists the solution identified for mitigation. The Cost Estimate is the estimated cost (dollars) to provide traditional solution identified.
Substation | Circuit | Violation Type | Operating Date | Traditional Solution | Cost Estimate
Kahului 5 | Kahului 8/4049 | Voltage | 2021 | LTC setting change | -
Kihei 4 | Kihei 35/1515 | Voltage | 2025 | LTC setting change | -
Kuau | Kuau 73/4066 | Voltage | 2021 | LTC setting change | -
Kuihelani | Kuihelani 209/1653 | Voltage | 2021 | LTC setting change | -
Kuihelani | Kuihelani 209/1708 | Voltage | 2021 | LTC setting change | -
Kula | Kula 13/1237 | Voltage, conductor overloading | 2022 | Reconductor and Install two 3ph line regulators | 2235909
Kula | Kula 13/1238 | Voltage | 2025 | LTC setting change | -
Lahaina 5 | Lahaina 34/1398 | Voltage | 2021 | Install 3ph line regulator | 210000
Paia Mauka | Paia Mauka 93/4042 | Voltage | 2021 | Circuit phase balancing | 3600
Peahi | Peahi 94/1294 | Voltage | 2021 | LTC setting change | -
Pukalani 1 | Pukalani 17/1282 | Voltage | 2022 | LTC setting change | -
Spreckelsville | Spreckelsville 92/4043 | Voltage | 2021 | LTC setting change | -
Waiinu 3 | Waiinu 36/1493 | Voltage | 2022 | LTC setting change | -
Wailea 4 | Wailea 25/1517 | Voltage | 2023 | LTC setting change | -
Wailea 4 | Wailea 25/1518 | Voltage | 2023 | LTC setting change | -

## Lanai GNA
Return to Assumptions Summary
Lana‘i Island Grid Needs Assessment - Base Forecast
The Grid Needs Assessment shows the grid needs identified for each circuit for the next 5 years (years 2021 through 2025). The Violation Type indicates whether a thermal and/or voltage violation triggers the grid need. The Operating Date indicates the date at which traditional infrastructure must be constructed and energized, in advance of the forecasted grid need to maintain safety and reliability. The Traditional Solution lists the solution identified for mitigation. The Cost Estimate is the estimated cost (dollars) to provide traditional solution identified.
Substation | Circuit | Violation Type | Operating Date | Traditional Solution | Cost Estimate
Miki Basin | Miki Basin PP 302/1208 | Voltage | 2023 | Install 3ph line regulator | 252000
Miki Basin | Miki Basin PP 302/1210 | Voltage | 2023 | Install 3ph line regulator | 252000

## Molokai GNA
Return to Assumptions Summary
Moloka‘i Island Grid Needs Assessment - Base Forecast
The Grid Needs Assessment shows the grid needs identified for each circuit for the next 5 years (years 2021 through 2025). The Violation Type indicates whether a thermal and/or voltage violation triggers the grid need. The Operating Date indicates the date at which traditional infrastructure must be constructed and energized, in advance of the forecasted grid need to maintain safety and reliability. The Traditional Solution lists the solution identified for mitigation. The Cost Estimate is the estimated cost (dollars) to provide traditional solution identified.
Substation | Circuit | Violation Type | Operating Date | Traditional Solution | Cost Estimate
Palaau | Palaau PP 81/109B | Voltage | 2023 | Install 3ph line regulator | 252000
Palaau | Palaau PP 81/110B | Voltage | 2021 | Install 3ph line regulator | 252000
Palaau | Palaau PP 81/111A | Voltage | 2021 | Install three 3ph line regulator | 756000