## Assumptions Summary
2020-2021 Distribution DER Hosting Capacity Grid Needs High DER Forecast
This workbook presents the IGP Distribution DER Hosting Capacity Grid Needs Report Tables; the DER growth and the hosting capacity analysis results. The Scenarios worksheet describes the DGPV forecast that corresponds to each scenario.
Version History
Date | Version | Description
2021-08-03 | 1 | First Release of the Draft Distribution DER Hosting Capacity Grid Needs Report Tables from the August 2021 Update. --Based on Corporate Forecast from March 2021
2021-10-08 | 2 | Revised Draft Distribution DER Hosting Capacity Grid Needs Report Tables from the October 2021 Update. --Based on Corporate Forecast from the August Update (submitted August 19, 2021). Includes the High DER forecast sensitivity.
2021-11-05 | 3 | Distribution DER Hosting Capacity Grid Needs Report Tables from the November 2021 Update. --Based on Corporate Forecast from the August Update (submitted August 19, 2021). Includes the High DER forecast sensitivity. --Includes revisions since the October 2021 Update.
Worksheet Descriptions
Worksheet | Category | Description | Source
Assumptions Summary | Assumptions Summary | Includes Workbook Version History, Worksheet Descriptions, and References | HECO
Glossary | Glossary | Definitions of All Acronyms and Common Terms Used in the Workbook | HECO
References | References | Provides Links to All Pertinent and Related Documents and Workbooks | HECO
Scenarios | Scenarios | Scenarios for Current Exisiting Modeling Cases | HECO
Oahu DER Growth | Adjusted DER Growth by Island | O‘ahu Adjusted DER Growth - High Forecast | HECO
Hawaii Island DER Growth |  | Hawai‘i Island Adjusted DER Growth - High Forecast | HECO
Maui Island DER Growth |  | Maui Island Adjusted DER Growth - High Forecast | HECO
Lanai DER Growth |  | Lana‘I Adjusted DER Growth - High Forecast | HECO
Molokai DER Growth |  | Moloka‘i Adjusted DER Growth - High Forecast | HECO
Oahu Circuit DER Growth | Adjusted DER Growth by Circuit | O‘ahu Adjusted DER Growth by Circuit - High Forecast | HECO
Hawaii Island Circuit DER Growth |  | Hawai‘i Island Adjusted DER Growth by Circuit - High Forecast | HECO
Maui Total DER Growth |  | Maui Island Adjusted DER Growth by Circuit - High Forecast | HECO
Lanai Circuit DER Growth |  | Lana‘I Adjusted DER Growth by Circuit - High Forecast | HECO
Molokai Circuit DER Growth |  | Moloka‘i Adjusted DER Growth by Circuit - High Forecast | HECO
Summary HC Results | Hosting Capacity Results | Summary of Hosting Capacity Results (All Islands) - High Forecast | HECO
O‘ahu HC Results |  | O‘ahu Hosting Capacity Analysis Results by Circuit - High Forecast | HECO
Hawai‘i Island HC Results |  | Hawai‘i Island Hosting Capacity Analysis Results by Circuit - High Forecast | HECO
Maui Island HC Results |  | Maui Island Hosting Capacity Analysis Results by Circuit - High Forecast | HECO
Lana‘i HC Results |  | Lana‘i Hosting Capacity Analysis Results by Circuit - High Forecast | HECO
Moloka‘i HC Results |  | Moloka‘i Hosting Capacity Analysis Results by Circuit - High Forecast | HECO
O‘ahu Total DER | DER Growth by Circuit and Hosting Capacity | O‘ahu Total DER Growth by Circuit; Executed and Updated Hosting Capacity - High Forecast | HECO
Hawai‘i Island Total DER |  | Hawai‘i Island Total DER Growth by Circuit; Executed and Updated Hosting Capacity - High Forecast | HECO
Maui Island Total DER |  | Maui Total DER Growth by Circuit; Executed and Updated Hosting Capacity - High Forecast | HECO
Lana‘i Total DER |  | Lana‘i Total DER Growth by Circuit; Executed and Updated Hosting Capacity - High Forecast | HECO
Moloka‘i Total DER |  | Moloka‘i Total DER Growth by Circuit; Executed and Updated Hosting Capacity - High Forecast | HECO
Summary GNA | Grid Needs Assessment Results | Summary of Grid Needs Assessment Results (All Islands) - High Forecast | HECO
O‘ahu GNA |  | O‘ahu Grid Needs Assessment Results by Circuit - High Forecast | HECO
Hawai‘i Island GNA |  | Hawai‘i Island Grid Needs Assessment Results by Circuit - High Forecast | HECO
Maui Island GNA |  | Maui Grid Needs Assessment Results by Circuit - High Forecast | HECO
Lana‘i GNA |  | Lana‘i Grid Needs Assessment Results by Circuit - High Forecast | HECO
Moloka‘i GNA |  | Moloka‘i Grid Needs Assessment Results by Circuit - High Forecast | HECO

## Glossary
Glossary |  | Return to Assumptions Summary
Acronym/ Terminology | Definition
8760 | 365 days/year x 24 hours/day = 8760 hours/year
Base Load | Created using historical load data and serves as the basis for creating the location-based forecasts
CBRE Phase 2 Small Projects | Community Based Renewable Energy Phase 2 small projects < 250 kW
CGS | Customer Grid Supply
CGS+ | Customer Grid Supply Plus
Conductor Overload Violation | Circuit condition exceeding thermal rating of conductors
CSS | Customer Self Supply
DBESS | Distributed Battery Energy Storage System
DER | Distributed Energy Resources
DER/BESS | Combined DER and DBESS
DGPV | Distributed Generation Photovoltaics
DR | Demand Response
EDR | Emergency Demand Response
EE | Energy Efficiency
EoT | Electrification of Transportation
EV | Electric Vehicle
Executed DER | DER that has been installed and energized on the system
Fct | Forecast, Forecasted
FIT | Feed-In Tariff
Gross Load | Load Without the Impacts of DER
Historical Peak Demand | Peak load determined using the historical data for the circuit or transformer
LDV | Light Duty Vehicle
LTC | Load Tap Changer
Managed Charging | Charging during hours of higher renewable penetration and lower system cost through rates and/or demand response (DR) programs
MVA | Megavolt-amperes. Unit of Apparent Power
MW | Megawatt, Unit of Real Power/ Capacity
NEM | Net Energy Metering
NEM+ | Net Energy Metering Plus
Net Load | Underlying Load Plus the Impacts of DGPV, DBESS, EE, and EV, Load Layers
PPA | Power Purchase Agreement
PV | Utility-scale Photovoltaic Generator
Rating | Represents the Assumed Power (MW) Produced in Every Hour
Schedule-G | General Service Non-Demand Rate (Small Commercial Customer)
Schedule-J | General Service Demand Rate (Medium Commercial Customer)
Schedule-P | Large Power Service Rate (Large Commercial Customer)
Schedule-R | Residential Service Rate (Residential Customer)
SE | Smart Export
Service Requests | Request for electrical service including location and estimated demand information
SIA | Standard Interconnection Agreement
Solar | Utility-scale Photovoltaic Generator
Total Anticipated DER | Executed DER + Forecasted DER
Underlying Load | Load based on customer-level sales forecast
Voltage Violation | Circuit condition where voltage exceeds (low and/or high) tariff limits

## References
References |  | Return to Assumptions Summary
Source | Materials
Distribution DER Hosting Capacity Grid Needs Report August 3, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/distribution_der_hosting_capacity_grid_needs_03Aug2021.pdf
Distribution DER Hosting Capacity Grid Needs Report Tables August 3, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/Distribution%20DER%20Hosting%20Capacity%20Grid%20Needs%2003Aug2021%20Report%20Tables.xlsx
Distribution Planning Methodology | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/stakeholder_engagement/working_groups/distribution_planning/20200602_dpwg_distribution_planning_methodology.pdf
Revised Draft IGP Inputs and Assumptions Document, August 3, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/20210803_heco_submittal_of_igp_inputs_and_assum_and_der_hosting_capacity.pdf
Revised Draft IGP Inputs and Assumptions Document, August 19, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/stakeholder_engagement/working_groups/forecast_assumptions/20210819_heco_submittal_of_revised_igp_inputs_and_assumptions.pdf
Distribution DER Hosting Capacity Grid Needs Report October 2021 Update | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/20211008_distribution_der_hosting_capacity_grid_needs_draft.pdf
Distribution DER Hosting Capacity Grid Needs Report Tables October 8, 2021 | https://www.hawaiianelectric.com/documents/clean_energy_hawaii/integrated_grid_planning/Revised%202021-10-08%20Distribution%20DER%20Hosting%20Capacity%20Grid%20Needs%20High%20Forecast.xlsx

## Scenarios
|  |  | Forecast Types | Return to Assumptions Summary
No. | Modeling Case | Purpose | DER Forecast
1 | Base | Reference Case | Base Forecast
2 | High Load Customer Technology Adoption Bookend | Understand the impact of customer adoption of technologies for DER, electric vehicles, energy efficiency, and time-of-use rates that lead to higher loads. | Low Forecast
3 | Low Load Customer Technology Adoption Bookend | Understand the impact of customer adoption of technologies for DER, electric vehicles, energy efficiency, and time-of-use rates that leads to lower loads. | High Forecast

## Oahu DER Growth
Return to Assumptions Summary
O‘ahu Adjusted DER Growth - High Forecast
The Adjusted DER Growth shows the annual DER corporate forecast and the adjustments made to account for projects not included in the corporate forecast. Adjustments are included for CBRE Phase 2 small projects or pending known large projects (such as CBRE Phase 1, FIT, and large SIA (> 250 kW)). The forecast is shown by system peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth
Forecasted DER Growth
Year | Corporate DER Forecast (Cumulative kW) | Adjustment for CBRE Phase 2 Small Projects (Cumulative kW) | Adjustment for Large Projects (Cumulative kW) | Adjusted DER Growth (Incremental kW)
kW | A | B | C | D = (A+B+C)1 - (A+B+C)0
2020 | 534703.6864 | 0 | 0 | n/a
2021 | 599747.9252 | 6000 | 29822 | 100866.2388
2022 | 702500.0001 | 12000 | 35025 | 113955.0749
2023 | 767994.0001 | 18000 | 35025 | 71494
2024 | 817264.0001 | 24000 | 39694 | 59939
2025 | 865746.0001 | 30000 | 39694 | 54482

## Hawaii Island DER Growth
Return to Assumptions Summary
Hawai‘i Island Adjusted DER Growth - High Forecast
The Adjusted DER Growth shows the annual DER corporate forecast and the adjustments made to account for projects not included in the corporate forecast. Adjustments are included for CBRE Phase 2 small projects or pending known large projects (such as CBRE Phase 1, FIT, and large SIA (> 250 kW)). The forecast is shown by system peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth
Forecasted DER Growth
Year | Corporate DER Forecast (Cumulative kW) | Adjustment for CBRE Phase 2 Small Projects (Cumulative kW) | Adjustment for Large Projects (Cumulative kW) | Adjusted DER Growth (Incremental kW)
kW | A | B | C | D = (A+B+C)1 - (A+B+C)0
2020 | 110107.527 | 0 | 0 | n/a
2021 | 123313.357 | 1500 | 850 | 15555.83
2022 | 137922.937 | 3000 | 850 | 16109.58
2023 | 151290.937 | 4500 | 850 | 14868
2024 | 164333.937 | 6000 | 850 | 14543
2025 | 177644.937 | 7500 | 850 | 14811

## Maui Island DER Growth
Return to Assumptions Summary
Maui Island Adjusted DER Growth - High Forecast
The Adjusted DER Growth shows the annual DER corporate forecast and the adjustments made to account for projects not included in the corporate forecast. Adjustments are included for CBRE Phase 2 small projects or pending known large projects (such as CBRE Phase 1, FIT, and large SIA (> 250 kW)). The forecast is shown by system peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth
Forecasted DER Growth
Year | Corporate DER Forecast (Cumulative kW) | Adjustment for CBRE Phase 2 Small Projects (Cumulative kW) | Adjustment for Large Projects (Cumulative kW) | Adjusted DER Growth (Incremental kW)
kW | A | B | C | D = (A+B+C)1 - (A+B+C)0
2020 | 119232.3133 | 0 | 0 | n/a
2021 | 132369.525 | 1695 | 1750 | 16582.2118
2022 | 147482.525 | 3390 | 1750 | 16808
2023 | 162214.525 | 5085 | 1750 | 16427
2024 | 176169.525 | 6780 | 1750 | 15650
2025 | 189796.525 | 8475 | 1750 | 15322

## Lanai DER Growth
Return to Assumptions Summary
Lana‘i Adjusted DER Growth - High Forecast
The Adjusted DER Growth shows the annual DER corporate forecast and the adjustments made to account for projects not included in the corporate forecast. Adjustments are included for CBRE Phase 2 small projects or pending known large projects (such as CBRE Phase 1, FIT, and large SIA (> 250 kW)). The forecast is shown by system peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth
Forecasted DER Growth
Year | Corporate DER Forecast (Cumulative kW) | Adjustment for CBRE Phase 2 Small Projects (Cumulative kW) | Adjustment for Large Projects (Cumulative kW) | Adjusted DER Growth (Incremental kW)
kW | A | B | C | D = (A+B+C)1 - (A+B+C)0
2020 | 832.72 | 0 | 0 | n/a
2021 | 887.72 | 0 | 0 | 55
2022 | 948.72 | 0 | 0 | 61
2023 | 1086.72 | 0 | 0 | 138
2024 | 1151.72 | 0 | 0 | 65
2025 | 1293.72 | 0 | 0 | 142

## Molokai DER Growth
Return to Assumptions Summary
Moloka‘i Adjusted DER Growth - High Forecast
The Adjusted DER Growth shows the annual DER corporate forecast and the adjustments made to account for projects not included in the corporate forecast. Adjustments are included for CBRE Phase 2 small projects or pending known large projects (such as CBRE Phase 1, FIT, and large SIA (> 250 kW)). The forecast is shown by system peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth
Forecasted DER Growth
Year | Corporate DER Forecast (Cumulative kW) | Adjustment for CBRE Phase 2 Small Projects (Cumulative kW) | Adjustment for Large Projects (Cumulative kW) | Adjusted DER Growth (Incremental kW)
kW | A | B | C | D = (A+B+C)1 - (A+B+C)0
2020 | 2678.3 | 0 | 0 | n/a
2021 | 3015.3 | 0 | 250 | 587
2022 | 3360.3 | 0 | 250 | 345
2023 | 3642.3 | 0 | 250 | 282
2024 | 3962.3 | 0 | 250 | 320
2025 | 4212.3 | 0 | 250 | 250

## Oahu Circuit DER Growth
Return to Assumptions Summary
O‘ahu Adjusted DER Growth by Circuit - High Forecast
The Adjusted DER Growth by Circuit shows the annual DER growth by circuit. The forecast is shown by circuit (or feeder) peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth (kW)
Circuit | 2021 | 2022 | 2023 | 2024 | 2025
AALA | 127.561 | 219.262 | 141.754 | 135.565 | 120.342
AALAPAPA | 197.451 | 450.042 | 240.093 | 192.603 | 203.325
AHUA | 235.524 | 318.662 | 115.018 | 242.058 | 101.937
AHUI | 0 | 0 | 0 | 0 | 0
AIEA | 293.595 | 434.06 | 243.156 | 299.258 | 397.701
AIEA 2 | 40.785 | 67.886 | 35.028 | 22.238 | 42.987
AIEA 3 | 48.551 | 68.03 | 128.033 | 112.026 | 66.931
AINA KOA | 592.727 | 709.356 | 593.709 | 253.695 | 591.167
AINONI | 76.114 | 87.876 | 95.194 | 76.545 | 69.849
AIRPORT | 300 | 300 | 107.564 | 200 | 7.564
AIRPORT 1 | 100 | 0 | 0 | 0 | 0
AIRPORT 2 | 100 | 0 | 0 | 0 | 0
ALA MOANA | 0 | 100 | 100 | 0.637 | 0
ALEWA | 28.694 | 56.461 | 47.979 | 18.793 | 30.533
ALIAMANU | 474.854 | 372.12 | 397.449 | 320.832 | 268.253
ANOI | 282.036 | 258.507 | 246.736 | 159.138 | 146.291
ANUU | 325.275 | 462.706 | 455.946 | 436.831 | 284.594
ARCHER 1 | 200 | 0 | 0 | 100 | 100
ARCHER 2 | 200 | 0 | 0 | 105.956 | 0
ARCHER 3 | 514.038 | 414.461 | 101.906 | 101.906 | 123.786
ARCHER 4 | 0 | 0 | 0 | 100 | 0
AUDITORIUM | 132.766 | 468.798 | 33.744 | 32.338 | 226.714
BARBERS PT | 405.017 | 236.522 | 109.316 | 93.297 | 206.068
BAY DR | 80.173 | 93.867 | 86.782 | 34.67 | 50.093
BEACH LOTS | 434.391 | 424.289 | 446.59 | 347.928 | 247.425
BECKLEY | 22.491 | 22.286 | 25.216 | 10.688 | 8.044
BLACK PT | 40.465 | 15.225 | 26.156 | 10.035 | 25.529
BWS | 151.366 | 265.836 | 150.693 | 129.272 | 236.176
CARLOS LONG | 301.749 | 264.667 | 285.506 | 197.618 | 170.956
CASTNER | 277.004 | 234.298 | 204.69 | 121.691 | 232.421
CEIP 3 | 999.634 | 322.68 | 0 | 0 | 100
CEIP 4 | 98.518 | 183.915 | 133.258 | 116.209 | 82.313
CKT 10 | 0 | 100 | 0 | 0 | 0
CKT 12 | 0 | 0 | 0 | 200 | 0
CKT 16 | 4074.595 | 1000 | 300 | 301.398 | 101.398
CKT 18 | 258.854 | 402.423 | 165.547 | 140.111 | 136.614
CKT 6 | 0 | 0 | 0 | 0 | 0
CKT 7 | 369.573 | 184.9 | 269.243 | 147.182 | 153.015
CKT 8 | 0 | 100 | 0 | 0 | 0
COCONUT GROVE | 83.57 | 214.769 | 106.994 | 61.263 | 55.418
DAIRYMENS | 100.647 | 73.806 | 65.378 | 70.996 | 75.818
DE RUSSY | 100 | 100 | 0 | 0 | 0
DEPOT RD | 198.013 | 238.607 | 226.352 | 141.233 | 129.245
DIAMOND HEAD | 356.179 | 983.678 | 524.513 | 59.767 | 494.563
DOLE 1 | 4.386 | 251.393 | 6.714 | 0 | 2.328
EKEKELA | 52.329 | 100.641 | 64.962 | 49.642 | 58.059
ENA 1 | 28.604 | 147.499 | 54.758 | 38.201 | 133.872
ENA 2 | 0 | 0 | 0 | 0 | 0
ENCHANTED LAKES | 315.561 | 436.183 | 221.61 | 265.997 | 216.908
EWA BEACH 1 | 675.72 | 815.028 | 744.118 | 462.471 | 402.44
EWA BEACH 2 | 451.578 | 542.554 | 401.302 | 349.207 | 346.348
EWA BEACH 3 | 355.558 | 838.1 | 610.525 | 347.149 | 229.073
EWA BEACH 4 | 572.296 | 1038.831 | 1027.726 | 671.418 | 504.959
EWA NUI 1 | 692.205 | 584.987 | 438.065 | 344.619 | 321.674
EWA NUI 2 | 652.057 | 1515 | 1344.548 | 513.42 | 523.474
FARMERS RD | 174.114 | 130.023 | 269.949 | 53.223 | 171.843
FORT ST | 11.61 | 16.685 | 13.37 | 106.582 | 11.706
FORT ST 1 | 200 | 100 | 0 | 0 | 0
FORT ST 2 | 17.144 | 137.809 | 28.315 | 11.577 | 21.452
FORT ST 3 | 14.266 | 40.22 | 112.112 | 6.842 | 3.73
FORT ST 4 | 123.63 | 274.99 | 217.299 | 68.138 | 83.963
FORT WEAVER 1 | 378.101 | 720.304 | 591.211 | 489.453 | 326.104
FORT WEAVER 2 | 773.93 | 756.681 | 699.561 | 494.256 | 440.874
FORT WEAVER 3 | 470.297 | 901.845 | 483.063 | 571.144 | 481.361
FORT WEAVER 4 | 360.391 | 432.718 | 352.981 | 268.027 | 235.959
HAHAIONE | 136.95 | 571.875 | 273.788 | 263.161 | 163.311
HALA 1 | 575.662 | 254.072 | 106.061 | 98.41 | 90.387
HALA 2 | 219.534 | 300.046 | 171.432 | 139.531 | 96.827
HALA 3 | 495.8 | 500.95 | 329.039 | 207.059 | 187.471
HALA 4 | 198.918 | 123.882 | 218.487 | 90.938 | 69.187
HALAWA | 225.884 | 477.389 | 168.619 | 309.425 | 209.531
HALEKOU | 297.996 | 359.232 | 271.73 | 250.451 | 196.963
HANUA 1 | 0 | 0 | 0 | 0 | 0
HANUA 2 | 0 | 0 | 0 | 0 | 0
HAUULA | 5008.8 | 217.437 | 164.362 | 111.798 | 105.571
HAWN PINE | 666 | 300 | 100 | 0 | 114.31
HAWN VILLAGE 1 | 0 | 103.156 | 2.104 | 1.052 | 100
HAWN VILLAGE 2 | 73.863 | 146.497 | 131.816 | 66.048 | 42.295
HEEIA | 382.748 | 505.93 | 305.018 | 239.23 | 291.354
HEIGHTS | 63.764 | 94.07 | 81.828 | 57.902 | 73.328
HELEMANO | 624.371 | 208.308 | 172.431 | 157.078 | 118.889
HIGHLANDS | 457.068 | 635.591 | 541.743 | 408.884 | 310.128
HIKINA | 9.388 | 68.178 | 11.406 | 16.31 | 13.532
HILA 1 | 103.841 | 218.549 | 522.77 | 114.697 | 14.139
HILA 2 | 164.29 | 223.816 | 117.729 | 60.621 | 72.267
HILA 3 | 408.326 | 225.948 | 200 | 8.067 | 102.705
HILA 4 | 0 | 0 | 0 | 0 | 0
HILA 5 | 439.36 | 212.925 | 146.671 | 300.77 | 402.844
HILA 6 | 0 | 0 | 0 | 0 | 0
HOAEAE 1 | 668.831 | 1042.912 | 763.058 | 575.058 | 605.981
HOAEAE 2 | 10.242 | 169.244 | 154.685 | 316.348 | 13.156
HOAEAE 3 | 955.625 | 418.101 | 391.408 | 751.045 | 386.726
HOUGHTAILING | 63.825 | 93.809 | 138.18 | 438.533 | 131.861
HUNAKAI | 40.49 | 167.761 | 58.95 | 30.921 | 33.249
ILANIWAI | 204.146 | 100 | 0 | 0 | 2.073
ILIAINA | 118.889 | 212.693 | 57.607 | 64.218 | 170.127
ILIKAI | 67.366 | 103.86 | 67.904 | 79.919 | 73.014
INDUSTRIAL | 707.38 | 864.087 | 0 | 0 | 0
IWILEI 1 11KV | 128.391 | 617.245 | 210.168 | 300 | 266.951
IWILEI 13 | 0 | 0 | 0 | 0 | 0
IWILEI 9 | 0 | 0 | 0 | 0 | 0
KAALAKEI | 221.544 | 310.37 | 376.598 | 203.406 | 202.314
KAENA PT | 329.148 | 581.065 | 351.153 | 245.226 | 253.237
KAHAI | 1211.546 | 415.702 | 255.97 | 41.903 | 15.161
KAHALA | 287.88 | 447.606 | 143.115 | 306.3 | 72.412
KAHALA 3 | 4219.199 | 552.348 | 616.712 | 383.723 | 386.543
KAHALA MALL | 223.066 | 290.826 | 413.741 | 70.772 | 211.446
KAHALOA | 79.978 | 135.989 | 128.489 | 67.671 | 57.376
KAHE | 499.475 | 507.546 | 311.229 | 188.351 | 172.925
KAHUKU | 489.862 | 636.963 | 269.818 | 300.557 | 212.376
KAI-HARDING | 13.793 | 22.39 | 44.855 | 30.171 | 23.411
KAI-KAIMUKI | 39.835 | 67.04 | 51.788 | 28.954 | 40.155
KAILUA 1 | 552.807 | 421.13 | 495.136 | 120.651 | 395.601
KAILUA 2 | 671.777 | 1017.953 | 951.554 | 555.813 | 427.141
KAILUA HTS | 360.601 | 741.211 | 499.878 | 346.45 | 253.435
KAINALU | 312.325 | 441.216 | 186.949 | 128.922 | 75.796
KAI-WAIALAE | 67.653 | 125.225 | 53.513 | 56.298 | 72.715
KAI-WILHELMINA | 128.66 | 75.979 | 40.26 | 28.911 | 19.485
KAKAAKO 5 | 20.844 | 26.821 | 35.082 | 21.846 | 29.724
KAKAAKO 6 | 0 | 100 | 0 | 100 | 0
KAKAAKO 8 | 720 | 0 | 200 | 0 | 0
KAKAAKO 9 | 147.176 | 235.95 | 15.364 | 206.076 | 103.841
KALAHEO | 90.226 | 74.302 | 99.182 | 129.143 | 271.482
KALAHEO 1 | 0 | 100 | 0 | 100 | 0
KALAHEO 2 | 0 | 0 | 0 | 0 | 0
KALAKAUA | 325.931 | 121.395 | 25.285 | 18.437 | 11.67
KALAMA | 22.252 | 65.841 | 267.909 | 39.538 | 21.782
KALIA | 0 | 0 | 0 | 0 | 0
KALIHI | 7.914 | 106.595 | 5.276 | 105.276 | 11.871
KALIHI KAI | 57.919 | 274.382 | 122.09 | 19.158 | 50.723
KALIHI ST | 32.007 | 133.887 | 131.745 | 51.626 | 72.432
KALIHI UKA | 21.708 | 84.538 | 46.123 | 39.659 | 30.166
KALIHI VALLEY | 69.31 | 114.698 | 101.004 | 61.012 | 63.539
KALOI 1 | 100 | 0 | 300 | 0 | 200
KAM HWY | 103.799 | 149.491 | 80.731 | 143.239 | 111.789
KAM IV | 90.894 | 165.069 | 101.506 | 55.459 | 132.889
KAM TERRACE | 129.939 | 276.31 | 115.239 | 400.042 | 189.034
KAMAKEE | 5.419 | 8.068 | 1.155 | 2.31 | 4.264
KAMANI | 125.36 | 0 | 5.06 | 0 | 100
KAMOKILA 1 | 276.285 | 200 | 127.88 | 0 | 100
KAMOKILA 2 | 204.978 | 457.343 | 213.003 | 120.232 | 288.123
KAMOKILA 3 | 916 | 300 | 0 | 0 | 149.324
KAMOKILA 4 | 245.599 | 359.137 | 328.274 | 223.757 | 195.723
KAMOKILA 5 | 0 | 700 | 215.687 | 222.773 | 0
KAMOKILA 6 | 115.984 | 196.18 | 181.03 | 121.054 | 111.008
KAMOKU 10 | 0 | 0 | 0 | 0 | 0
KAMOKU 9 | 0 | 0 | 0 | 0 | 0
KANAINA | 430.828 | 609.193 | 361.499 | 269.377 | 384.636
KANEKAPOLEI | 161.838 | 284.009 | 159.132 | 47.904 | 256.73
KANEOHE 5 | 139.115 | 207.506 | 167.088 | 149.958 | 169.944
KANEOHE 6 | 355.934 | 175.092 | 302.45 | 83.715 | 36.997
KAONOHI 1 | 343.385 | 473.161 | 149.249 | 142.825 | 258.56
KAONOHI 2 | 225.653 | 646.477 | 332.502 | 219.945 | 182.688
KAONOHI 3 | 50.671 | 80.087 | 59.972 | 58.517 | 58.51
KAONOHI 4 | 176.099 | 194.477 | 93.868 | 69.123 | 70.138
KAPAHULU 1 | 124.246 | 29.634 | 22.45 | 13.47 | 15.266
KAPAHULU 2 | 0 | 0 | 0 | 0 | 0
KAPAHULU 3 | 0 | 200 | 0 | 11.74 | 0
KAPAHULU 4 | 12.481 | 65.2 | 32.68 | 15.078 | 20.478
KAPALAMA | 34.022 | 48.838 | 35.152 | 25.608 | 14.335
KAP-HARDING | 66.606 | 88.212 | 71.494 | 71.929 | 43.59
KAPIOLANI 1 | 436.819 | 397.915 | 201.988 | 98.086 | 321.87
KAPIOLANI 2 | 349.534 | 306.635 | 322.591 | 113.035 | 107.233
KAPIOLANI 3 | 447.318 | 427.04 | 379.003 | 412.01 | 104.521
KAP-KAIMUKI | 6.066 | 23.125 | 23.382 | 108.651 | 115.414
KAPOLEI 1 | 100 | 0 | 0 | 0 | 0
KAPOLEI 2 | 284.918 | 346.088 | 263.619 | 239.564 | 223.942
KAPOLEI 3 | 522.196 | 144.297 | 124.106 | 222.196 | 115.186
KAPOLEI 4 | 5153.199 | 198.804 | 141.854 | 86.853 | 100.48
KAP-WAIALAE | 33.776 | 446.793 | 39.238 | 140.267 | 23.249
KAUHALE | 608.69 | 146.762 | 264.694 | 68.414 | 44.696
KAWAILOA | 114.264 | 389.589 | 122.754 | 85.112 | 98.673
KAWELA | 264.456 | 207.252 | 167.963 | 63.553 | 464.474
KEALAOLU | 34.894 | 43.483 | 22.281 | 37.136 | 27.435
KEAWE | 17.743 | 128.518 | 329.351 | 15.386 | 26.712
KEEHI 1 | 0 | 217.06 | 0 | 39.225 | 0
KEEHI 5 | 100 | 300 | 200 | 0 | 300
KEEHI 6 | 0 | 336.799 | 5.555 | 200 | 105.475
KEEHI 7 | 263 | 200 | 100 | 0 | 0
KEEHI 8 | 100 | 100 | 100 | 100 | 0
KEOLU DR | 334.338 | 279.133 | 223.775 | 173.069 | 322.81
KEWALO | 237.524 | 327.755 | 266.075 | 4849.245 | 198.912
KEWALO 1 | 26.324 | 126.645 | 14.357 | 16.889 | 113.871
KEWALO 2 | 30.323 | 129.247 | 31.723 | 18.574 | 27.197
KEWALO 3 | 0 | 0 | 0 | 0 | 0
KEWALO 4 | 122.668 | 134.29 | 40.007 | 118.81 | 21.563
KEWALO 5 | 0 | 0 | 0 | 0 | 0
KEWALO 6 | 0 | 0 | 0 | 0 | 0
KEWALO 7 | 0 | 0 | 0 | 0 | 0
KILAUEA 12KV | 214.916 | 125.341 | 97.671 | 119.242 | 110.052
KILAUEA 4KV | 73.467 | 84.793 | 63.609 | 61.669 | 78.128
KIPAPA | 374.849 | 166.023 | 61.73 | 250.764 | 143.249
KO OLINA 1 | 171.51 | 89.166 | 59.974 | 42.571 | 43.168
KO OLINA 2 | 0 | 0 | 0 | 0 | 0
KO OLINA 3 | 200 | 200 | 0 | 0 | 100
KOKOHEAD | 163.155 | 219.9 | 207.659 | 131.196 | 145.917
KOLOA | 160.118 | 187.8 | 266.805 | 175.201 | 150.611
KONA ST | 0 | 0 | 0 | 0 | 0
KUAHELANI 1 | 163.692 | 428.742 | 244.45 | 141.466 | 166.142
KUAHELANI 2 | 102.027 | 248.679 | 153.203 | 75.501 | 98.401
KUAHELANI 3 | 196.168 | 317.417 | 270.711 | 176.713 | 193.786
KUAHELANI 4 | 334.649 | 503.936 | 497.034 | 293.381 | 321.109
KUAKINI | 19.462 | 16.36 | 27.047 | 12.066 | 10.635
KUAPA 1 | 207.771 | 278.492 | 230.809 | 197.17 | 219.58
KUAPA 2 | 335.324 | 322.581 | 360.818 | 258.004 | 102.627
KUAPA 3 | 180.56 | 258.831 | 202.289 | 130.352 | 149.747
KUAPA 4 | 253.43 | 341.211 | 227.664 | 148.016 | 244.307
KUHIO | 13.017 | 17.418 | 10.059 | 10.5 | 6.613
KUHIO 1 | 19.142 | 125.457 | 21.388 | 11.201 | 8.885
KUHIO 2 | 0 | 200 | 300 | 0 | 100
KUHIO 3 | 0 | 102.44 | 4.88 | 0 | 0
KUHIO 4 | 57.447 | 379.624 | 70.83 | 39.548 | 57.101
KUILIMA 1 | 121.415 | 185.441 | 261.24 | 142.253 | 118.134
KUNIA | 9.364 | 219.561 | 30.194 | 12.765 | 19.661
KUNIA MAKAI 1 | 160.271 | 212.802 | 195.068 | 134.687 | 122.107
KUNIA MAKAI 2 | 766.844 | 997.278 | 479.587 | 626.562 | 353.653
KUNIA MAKAI 3 | 378.634 | 582.435 | 268.187 | 296.457 | 301.511
KUNIA MAKAI 4 | 102.994 | 146.569 | 125.549 | 103.135 | 108.217
LAGOON | 304.043 | 208.086 | 0 | 200 | 404.043
LAKESIDE 1 | 309.86 | 502.219 | 435.537 | 630.195 | 383.447
LAKESIDE 2 | 111.601 | 144.041 | 121.352 | 97.982 | 91.912
LAKESIDE 3 | 193.844 | 344.001 | 203.364 | 245.551 | 179.775
LAKESIDE 4 | 283.679 | 256.352 | 109.865 | 89.031 | 173.933
LANIKAI | 3.879 | 0 | 0 | 0 | 0
LAULIMA | 169.56 | 333.062 | 190.395 | 134.321 | 119.504
LEAHI | 307.701 | 430.647 | 522.548 | 230.895 | 286.464
LEOMELE | 204.838 | 330.073 | 264.796 | 192.099 | 165.682
LEOOLE | 113.247 | 825.308 | 380.362 | 211.727 | 213.247
LIBERTY HOUSE | 0 | 0 | 0 | 19.94 | 0
LIGHTHOUSE | 300 | 300 | 8.245 | 0 | 201
LIKELIKE | 43.944 | 81.558 | 72.286 | 44.713 | 44.854
LILIHA MAKAI | 2.886 | 29.234 | 10.873 | 13.89 | 6.513
LOWREY | 71.996 | 103.082 | 117.774 | 115.719 | 81.097
LUAWAI | 492.577 | 572.575 | 266.668 | 171.889 | 326.345
LUMIAUAU | 245.131 | 401.754 | 140.916 | 117.449 | 199.204
MACHADO ST | 45.678 | 91.611 | 69.298 | 51.023 | 53.759
MAHUKONA | 119.695 | 131.072 | 18.422 | 120.454 | 66.347
MAKAHA | 775.509 | 561.493 | 508.553 | 364.501 | 270.523
MAKAHA VALLEY | 174.875 | 390.442 | 200.332 | 62.79 | 159.089
MAKAKILO 1 | 434.303 | 507.392 | 490.871 | 313.977 | 319.972
MAKAKILO 2 | 696.026 | 3603.526 | 718.398 | 432.827 | 462.059
MAKAKILO 3 | 231.475 | 415.949 | 283.804 | 264.698 | 259.201
MAKAKILO 4 | 61.986 | 120.946 | 108.644 | 63.168 | 54.833
MAKALAPA-MOANALUA | 179.658 | 356.388 | 306.73 | 166.722 | 153.895
MAKALOA | 124.644 | 259.842 | 60.653 | 34.142 | 132.87
MALAKOLE | 0 | 0 | 0 | 0 | 0
MALAKOLE 4 | 516.571 | 2703.2 | 200 | 0 | 204.113
MANAGERS | 93.544 | 180.278 | 128.237 | 67.093 | 81.449
MANOA 1 | 95.574 | 173.423 | 142.507 | 103.269 | 138.758
MANOA 2 | 79.285 | 153.338 | 89.081 | 108.446 | 74.339
MANOA 3 | 235.553 | 200.253 | 147.97 | 217.704 | 212.321
MANOA 4 | 0 | 0 | 0 | 0 | 0
MANOA-MCCULLY | 28.749 | 40.952 | 27.877 | 23.169 | 22.065
MANOA-PIIKOI | 147.038 | 210.744 | 199.726 | 222.726 | 219.093
MAPUNAPUNA | 225.038 | 324.472 | 100 | 200 | 0
MAPUNAPUNA-MOANALUA | 264.817 | 182.876 | 241.345 | 146.584 | 149.307
MAUKA | 815.769 | 1213.598 | 767.522 | 543.316 | 911.386
MAUNALANI | 82.625 | 255.812 | 151.437 | 119.558 | 87.685
MAUNAWILI | 0 | 0 | 0 | 0 | 0
MCCULLY 1 | 203.336 | 463.455 | 193.525 | 198.603 | 189.545
MCCULLY 3 | 307.189 | 347.534 | 10.27 | 607.189 | 220.295
MCCULLY 5 | 105.338 | 167.092 | 175.7 | 83.726 | 79.656
MIKILUA 1 | 142.199 | 399.614 | 159.72 | 203.789 | 152.602
MIKILUA 3 | 252.881 | 436.61 | 477.141 | 207.015 | 288.143
MIKILUA 4 | 422.974 | 752.04 | 790.789 | 482.778 | 187.579
MIKILUA 5 | 510.498 | 760.966 | 659.579 | 556.851 | 548.712
MILILANI 1 | 200.482 | 296.731 | 238.659 | 148.249 | 176.889
MILILANI 2 | 222.068 | 321.21 | 207.431 | 177.592 | 210.713
MILILANI 3 | 77.258 | 216.775 | 92.736 | 70.311 | 188.435
MILILANI 4 | 370.503 | 402.085 | 311.268 | 242.419 | 221.856
MOILIILI 1 | 292.693 | 271.162 | 248.218 | 177.952 | 298.181
MOILIILI 2 | 163.614 | 243.071 | 186.55 | 179.701 | 154.429
MOKAUEA | 14.605 | 19.009 | 26.468 | 17.712 | 9.554
MOKUOLA | 508.078 | 833.743 | 164.782 | 269.375 | 334.859
MOKUONE 1 | 0 | 0 | 0 | 0 | 0
MOKUONE 2 | 0 | 209.09 | 100 | 100 | 0
NIU | 232.773 | 427.269 | 375.384 | 161.985 | 177.05
NUMANA | 50.868 | 56.704 | 62.919 | 34.655 | 34.048
NUUANU | 167.956 | 93.63 | 184.288 | 143.2 | 51.484
NUUANU 2 | 285.273 | 802.251 | 95.202 | 105.162 | 219.02
NUUANU 3 | 328.909 | 381.488 | 208.427 | 245.375 | 334.211
OCEAN POINTE 1 | 324.862 | 789.529 | 398.415 | 418.515 | 321.192
OCEAN POINTE 2 | 422.873 | 546.201 | 408.262 | 354.317 | 309.993
OCEAN POINTE 3 | 442.207 | 464.703 | 403.044 | 246.049 | 275.284
OCEAN POINTE 4 | 112.132 | 154.066 | 137.013 | 103.142 | 111.836
OLOMANA | 933.98 | 77.781 | 70.838 | 26.697 | 43.811
ONEAWA | 72.608 | 79.195 | 108.726 | 64.698 | 48.335
PAHIA | 406.386 | 266.05 | 200.528 | 117.842 | 245.329
PAIWA | 161.766 | 237.452 | 181.009 | 127.998 | 152.162
PALEKA | 115.27 | 216.708 | 124.027 | 76.263 | 105.439
PALI | 174.797 | 314.273 | 207.481 | 161.353 | 179.498
PAOAKALANI | 413.039 | 630.031 | 321.735 | 218.959 | 115.822
PAUOA 1 | 117.263 | 193.207 | 180.039 | 116.131 | 145.966
PAUOA 2 | 604.476 | 778.941 | 460.497 | 380.028 | 335.649
PAWAA KAI | 123.665 | 426.747 | 212.472 | 12.199 | 112.841
PAWAINA | 78.436 | 163.685 | 105.885 | 82.342 | 83.572
PEARL CITY 1 | 197.008 | 651.821 | 184.459 | 98.67 | 569.576
PEARL CITY 2 | 395.004 | 780.039 | 424.932 | 287.653 | 229.961
PENINSULA | 186.851 | 707.755 | 379.513 | 148.561 | 71.746
PENSACOLA | 255.765 | 278.549 | 184.275 | 159.549 | 151.755
PIIKOI | 151.916 | 212.598 | 198.505 | 135.331 | 132.877
PIIKOI 7 | 112.904 | 337.71 | 25.843 | 26.782 | 23.356
PIIKOI 8 | 222.617 | 367.806 | 261.384 | 272.964 | 136.843
POAMOHO | 0 | 0 | 0 | 0 | 0
POHAKUPU 4 | 192.479 | 498.072 | 231.048 | 298.782 | 376.783
PORTLOCK | 456.199 | 1563.64 | 609.129 | 914.655 | 670.559
PUNALUU | 188.215 | 511.386 | 283.935 | 494.123 | 206.642
PUNCHBOWL | 107.722 | 149.835 | 95.213 | 56.475 | 49.418
PUOHALA 1 | 107.818 | 263.843 | 145.737 | 137.387 | 89.007
PUOHALA 2 | 479.067 | 531.522 | 447.416 | 343.757 | 404.393
PUUHALE | 141.632 | 70.186 | 51.514 | 119.053 | 109.856
PUUNUI | 53.534 | 106.78 | 81.283 | 100.078 | 62.229
QUEEN ST | 200 | 8.064 | 0 | 0 | 0
QUEENS 1 | 184.074 | 233.382 | 220.12 | 111.198 | 135.894
QUEENS 2 | 190.699 | 97.591 | 80.447 | 77.852 | 53.919
RUGER | 37.187 | 55.185 | 29.903 | 34.645 | 27.913
SAND ISLAND | 209.098 | 58.164 | 25.58 | 209.748 | 52.459
SAND ISLAND 1 | 0 | 0 | 0 | 0 | 0
SAND ISLAND 2 | 363 | 100 | 0 | 0 | 0
SCHOOL ST | 241.235 | 430.226 | 202.41 | 171.394 | 122.164
SCHOOL ST 3 | 269.314 | 396.179 | 206.052 | 66.131 | 60.26
SHAFTER | 0.26 | 400 | 0 | 0 | 0
SHERATON 1 | 18.4 | 46.1 | 38.313 | 19.507 | 29.526
SHERATON 2 | 2.831 | 3.292 | 5.481 | 1.827 | 3.473
SHOPPING CTR | 0 | 29.04 | 0 | 0 | 0
SOUTH RAMP 1 | 625 | 400 | 100 | 400 | 400
ST LOUIS | 99.651 | 181.178 | 114.677 | 125.393 | 148.494
ST LOUIS HTS | 13.625 | 13.884 | 8.623 | 11.203 | 17.021
THURSTON | 157.073 | 261.285 | 222.437 | 225.593 | 246.301
TOWN | 3.244 | 1.622 | 1.622 | 0 | 2.433
UALENA | 14.689 | 21.559 | 6.87 | 0 | 100
UPLANDS | 148.073 | 103.554 | 90.492 | 64.27 | 63.036
UWAPO 1 | 350.652 | 409.759 | 329.947 | 223.262 | 198.062
UWAPO 2 | 73.736 | 132.875 | 112.63 | 79.641 | 77.484
UWAPO 3 | 273.332 | 412.311 | 309.035 | 200.017 | 275.98
UWAPO 4 | 0 | 2.987 | 0 | 0 | 3.353
WAHIAWA HTS | 281.239 | 533.237 | 354.101 | 325.482 | 250.085
WAHIAWA PROPER | 94.127 | 326.774 | 108.598 | 74.479 | 81.593
WAIAKAMILO 1 | 103.089 | 115.169 | 29.284 | 23.322 | 21.526
WAIAKAMILO 2 | 109.26 | 133.312 | 31.169 | 112.353 | 20.156
WAIAKAMILO 3 | 182.048 | 233.116 | 383.493 | 60.496 | 163.374
WAIAKAMILO 4 | 166.261 | 176.468 | 239.006 | 48.266 | 41.812
WAIAKAMILO-IWILEI | 49.622 | 294.355 | 77.086 | 48.424 | 48.343
WAIAKAMILO-KAPALAMA | 231.638 | 131.508 | 12.37 | 120.254 | 339.694
WAIALAE NUI | 167.026 | 212.052 | 180.233 | 149.181 | 170.489
WAIALAE SC | 0 | 0 | 0 | 0 | 0
WAIALUA | 141.877 | 308.766 | 446.464 | 161.817 | 247.686
WAIAWA 1 | 1023.806 | 260.549 | 412.342 | 164.671 | 122.915
WAIAWA 2 | 1009.894 | 200 | 0 | 100 | 116.337
WAIAWA 3 | 90.82 | 111.054 | 94.17 | 51.232 | 53.394
WAIAWA 4 | 248.124 | 448.052 | 185.365 | 234.957 | 153.228
WAIHEE 1 | 228.388 | 329.301 | 319.013 | 406.095 | 270.291
WAIHEE 2 | 244.078 | 310.809 | 277.977 | 154.72 | 153.036
WAIHEE 3 | 55.207 | 236.429 | 67.262 | 89.59 | 44.011
WAIHEE 4 | 406.309 | 451.41 | 410.21 | 275.695 | 280.874
WAIKELE CTR | 200 | 0 | 336.524 | 300 | 200
WAIKIKI 1 | 115.779 | 131.973 | 24.436 | 23.33 | 22.495
WAIKIKI 2 | 100 | 0 | 0 | 100 | 0
WAIKIKI 3 | 1.573 | 108.48 | 331.896 | 3.146 | 25.583
WAIKIKI 4 | 214.289 | 19.209 | 16.136 | 118.99 | 13.328
WAIKIKI 5 | 160.223 | 380.96 | 172.514 | 145.574 | 265.08
WAIKIKI 6 | 100 | 100 | 100 | 100 | 200
WAILANI | 135.499 | 205.335 | 130.827 | 36.487 | 129.991
WAILUPE | 753.625 | 1207.847 | 1135.862 | 444.763 | 322.815
WAIMALU 1 | 1989.948 | 287.18 | 160.74 | 89.239 | 86.46
WAIMALU 2 | 283.653 | 500.711 | 276.882 | 236.766 | 281.809
WAIMALU 3 | 444.634 | 640.509 | 502.407 | 355.995 | 343.957
WAIMALU 4 | 188.462 | 355.766 | 124.714 | 107.245 | 99.805
WAIMANALO | 272.202 | 554.355 | 187.08 | 154.826 | 251.222
WAIMANO 5 | 126.581 | 244.971 | 183.141 | 148.146 | 147.897
WAIMANO 6 | 186.487 | 503.499 | 222.664 | 157.43 | 151.921
WAIMANO HOME RD | 438.493 | 800.841 | 471.557 | 410.798 | 354.9
WAIMEA 1 | 32.597 | 58.714 | 74.983 | 39.948 | 46.794
WAIMEA 2 | 160.495 | 588.833 | 361.918 | 187.2 | 225.669
WAIOMAO | 565.071 | 504.761 | 312.208 | 334.632 | 460.244
WAIPAHU | 1056.851 | 1645.646 | 1280.445 | 1001.473 | 875.795
WAIPIO 1 | 133.529 | 220.085 | 102.373 | 150.691 | 93.742
WAIPIO 2 | 167.406 | 216.112 | 60.971 | 55.894 | 74.782
WAIWAI | 200 | 100 | 0 | 0 | 0
WAI-WILHELMINA | 63.471 | 106.481 | 110.382 | 53.945 | 87.908
WHITMORE | 9.232 | 8.333 | 11.453 | 10.617 | 4.989
WILIWILI | 136.444 | 213.191 | 155.961 | 98.413 | 129.673
WILIWILI 2 | 137.246 | 156.517 | 123.927 | 80.178 | 117.383
WOODLAWN | 76.394 | 94.749 | 74.901 | 59.584 | 70.527

## Hawaii Island Circuit DER Growt
Return to Assumptions Summary
Hawai‘i Island Adjusted DER Growth by Circuit - High Forecast
The Adjusted DER Growth by Circuit shows the annual DER growth by circuit. The forecast is shown by circuit (or feeder) peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth (kW)
Circuit | 2021 | 2022 | 2023 | 2024 | 2025
Ainaloa 11 | 91.9162 | 100.6901 | 92.9298 | 90.8985 | 92.5735
Ainaloa 12 | 64.6772 | 70.8509 | 65.3904 | 63.961 | 65.1397
Anaehoomalu 11 | 23.1287 | 25.3364 | 23.3837 | 22.8726 | 23.2941
Anaehoomalu 12 | 39.4206 | 43.1835 | 39.8553 | 38.9841 | 39.7025
Anaehoomalu 13 | 28.0806 | 30.761 | 28.3902 | 27.7696 | 28.2814
Captain Cook 11 | 193.6487 | 212.1335 | 195.7842 | 191.5045 | 195.0336
Captain Cook 12 | 147.9852 | 162.1112 | 149.6171 | 146.3467 | 149.0435
Hakalau 1 | 21.3212 | 23.3565 | 21.5564 | 21.0852 | 21.4737
Halaula 1 | 77.4408 | 84.8329 | 78.2948 | 76.5833 | 77.9946
Halaula 2 | 0 | 0 | 0 | 0 | 0
Hale Pohaku 11 | 30.7699 | 33.707 | 31.1092 | 30.4292 | 30.9899
Hale Pohaku 12 | 12.9801 | 14.2191 | 13.1232 | 12.8364 | 13.0729
Haleaha 11 | 62.5686 | 68.5411 | 63.2586 | 61.8758 | 63.0161
Haleaha 12 | 194.0531 | 212.5765 | 196.193 | 191.9044 | 195.4409
Hawaiian Beaches 11 | 98.7193 | 108.1426 | 99.8079 | 97.6262 | 99.4253
Hawaiian Beaches 12 | 0.72773 | 0.7972 | 0.73576 | 0.71967 | 0.73294
Hawaiian Paradise Park 11 | 92.6711 | 101.517 | 93.693 | 91.645 | 93.3338
Hawaiian Paradise Park 12 | 179.7453 | 196.9029 | 181.7275 | 177.7551 | 181.0308
Hawaiian Paradise Park 13 | 473.7573 | 518.98 | 478.9817 | 468.5116 | 477.1454
Hawaiian Paradise Park 14 | 80.4891 | 88.1722 | 81.3767 | 79.5979 | 81.0647
Hawi 11 | 63.2546 | 69.2926 | 63.9522 | 62.5543 | 63.707
Hawi 12 | 49.1045 | 53.7918 | 49.646 | 48.5608 | 49.4557
Honokaa 12 | 73.4854 | 80.4999 | 74.2957 | 72.6717 | 74.0109
Honokaa 14 | 98.3573 | 107.746 | 99.4419 | 97.2682 | 99.0607
Honomu 1 | 28.7625 | 31.508 | 29.0797 | 28.444 | 28.9682
Host Park 11 | 124.83 | 136.7456 | 126.2065 | 123.4478 | 125.7227
Host Park 12 | 0 | 0 | 0 | 0 | 0
Host Park 13 | 10.5204 | 11.5246 | 10.6364 | 10.4039 | 10.5956
Host Park 14 | 66.1575 | 72.4726 | 66.8871 | 65.425 | 66.6306
Huehue 11 | 727.3368 | 796.765 | 735.3576 | 719.2834 | 732.5384
Kahaluu 11 | 243.191 | 266.4049 | 245.8728 | 240.4983 | 244.9302
Kahaluu 12 | 137.2948 | 150.4003 | 138.8089 | 135.7746 | 138.2767
Kahaluu 14 | 34.0611 | 37.3124 | 34.4367 | 33.6839 | 34.3047
Kahaluu 15 | 221.7749 | 242.9445 | 224.2206 | 219.3193 | 223.361
Kailua 11 | 290.8591 | 318.6232 | 294.0666 | 287.6386 | 292.9392
Kailua 12 | 4.1018 | 4.4933 | 4.147 | 4.0563 | 4.1311
Kailua 15 | 389.3737 | 426.5415 | 393.6676 | 385.0624 | 392.1584
Kaloko 11 | 198.7782 | 217.7526 | 200.9702 | 196.5772 | 200.1997
Kaloko 12 | 38.3744 | 42.0374 | 38.7976 | 37.9495 | 38.6488
Kaloko 13 | 129.8248 | 142.2173 | 131.2565 | 128.3874 | 130.7533
Kaloko 14 | 5.5858 | 6.119 | 5.6474 | 5.524 | 5.6258
Kamuela 11 | 4.5596 | 4.9948 | 4.6099 | 4.5091 | 4.5922
Kamuela 12 | 147.4143 | 161.4858 | 149.0399 | 145.782 | 148.4685
Kanoelehua 11 | 88.7525 | 97.2244 | 89.7313 | 87.7698 | 89.3873
Kanoelehua 1101 | 95.5731 | 104.6961 | 96.6271 | 94.5149 | 96.2566
Kanoelehua 12 | 74.7123 | 81.844 | 75.5362 | 73.8851 | 75.2466
Kanoelehua 13 | 12.5699 | 13.7698 | 12.7085 | 12.4307 | 12.6598
Kanoelehua 14 | 143.0234 | 156.6757 | 144.6006 | 141.4398 | 144.0462
Kanoelehua 1401 | 132.3984 | 145.0365 | 133.8584 | 130.9324 | 133.3452
Kanoelehua 15 | 168.8763 | 184.9964 | 170.7386 | 167.0064 | 170.084
Kanoelehua 17 | 56.5739 | 61.9742 | 57.1978 | 55.9475 | 56.9785
Kapua 11 | 32.5873 | 35.698 | 32.9467 | 32.2265 | 32.8204
Kapua 12 | 87.3938 | 95.736 | 88.3575 | 86.4261 | 88.0188
Kauhale 11 | 111.8796 | 122.5591 | 113.1134 | 110.6408 | 112.6797
Kauhale 12 | 19.3557 | 21.2033 | 19.5691 | 19.1414 | 19.4941
Kaumana 11 | 285.0277 | 312.2351 | 288.1709 | 281.8717 | 287.0661
Kaumana 12 | 82.4561 | 90.3269 | 83.3654 | 81.5431 | 83.0458
Kawaihae 11 | 26.4769 | 29.0043 | 26.7689 | 26.1837 | 26.6662
Kawaihae 12 | 46.3698 | 50.796 | 46.8811 | 45.8564 | 46.7014
Kawaihae 13 | 2.2494 | 2.4641 | 2.2742 | 2.2244 | 2.2654
Kawailani 11 | 245.262 | 268.6736 | 247.9667 | 242.5464 | 247.016
Kawailani 12 | 234.3483 | 256.7181 | 236.9326 | 231.7535 | 236.0242
Keahole Airport 11 | 131.2697 | 143.8001 | 132.7173 | 129.8162 | 132.2085
Keahole Airport 12 | 36.593 | 40.086 | 36.9966 | 36.1879 | 36.8547
Keahole Airport 13 | 83.4261 | 91.3895 | 84.3461 | 82.5023 | 84.0227
Keahuolu 11 | 25.4139 | 27.8398 | 25.6941 | 25.1325 | 25.5956
Keahuolu 12 | 67.832 | 74.3069 | 68.58 | 67.0809 | 68.3171
Kealakehe 11 | 79.1151 | 86.6671 | 79.9876 | 78.2391 | 79.6809
Kealia 11 | 35.1032 | 38.454 | 35.4903 | 34.7145 | 35.3542
Kealia 12 | 58.8483 | 64.4657 | 59.4972 | 58.1967 | 59.2692
Keauhou 11 | 129.0945 | 141.4172 | 130.5181 | 127.6651 | 130.0177
Keauhou 13 | 143.6056 | 157.3135 | 145.1892 | 142.0155 | 144.6326
Komohana 12 | 382.419 | 418.9229 | 386.6361 | 378.1846 | 385.1539
Komohana 13 | 347.694 | 380.8832 | 351.5282 | 343.8441 | 350.1805
Komohana 14 | 26.7119 | 29.2617 | 27.0065 | 26.4161 | 26.9029
Kuakini 11 | 459.7138 | 503.596 | 464.7834 | 454.6237 | 463.0015
Kuakini 13 | 109.3155 | 119.7502 | 110.521 | 108.1051 | 110.0973
Kuakini 14 | 454.3765 | 497.7492 | 459.3872 | 449.3454 | 457.626
Kulani 12 | 3.7577 | 4.1164 | 3.7992 | 3.7161 | 3.7846
Kurtistown 12 | 110.3342 | 120.8662 | 111.5509 | 109.1125 | 111.1232
Lalamilo 11 | 85.7381 | 93.9223 | 86.6836 | 84.7888 | 86.3513
Lalamilo 12 | 31.7082 | 34.735 | 32.0579 | 31.3571 | 31.935
Laupahoehoe 1 | 10.478 | 11.4782 | 10.5936 | 10.362 | 10.553
Laupahoehoe 2 | 22.1806 | 24.2979 | 22.4252 | 21.935 | 22.3393
Maliu Ridge 11 | 40.4304 | 44.2897 | 40.8763 | 39.9828 | 40.7196
Maliu Ridge 12 | 50.4606 | 55.2773 | 51.017 | 49.9019 | 50.8215
Mauna Lani 11 | 287.2763 | 314.6983 | 290.4442 | 284.0954 | 289.3308
Mauna Lani 13 | 100.1181 | 109.675 | 101.2222 | 99.0096 | 100.8341
Mauna Lani 14 | 436.6395 | 478.3191 | 441.4546 | 431.8049 | 439.7622
Mountain View 11 | 116.7026 | 127.8425 | 117.9896 | 115.4104 | 117.5372
Mountain View 12 | 22.3424 | 24.4752 | 22.5888 | 22.0951 | 22.5022
Namakani Paio | 22.1853 | 24.303 | 22.4299 | 21.9396 | 22.3439
Ookala | 19.8135 | 21.7048 | 20.032 | 19.5941 | 19.9552
Orchid Isle 11 | 7.1437 | 7.8256 | 7.2225 | 7.0646 | 7.1948
Orchid Isle 12 | 40.5102 | 44.3771 | 40.957 | 40.0617 | 40.7999
Ouli 11 | 62.0105 | 67.9297 | 62.6943 | 61.3239 | 62.454
Ouli 12 | 116.6161 | 127.7477 | 117.9021 | 115.3249 | 117.4501
Paauilo 1 | 28.8379 | 31.5907 | 29.1559 | 28.5186 | 29.0442
Pahala 11 | 41.4014 | 45.3533 | 41.8579 | 40.943 | 41.6975
Pahala 12 | 8.2644 | 9.0533 | 8.3555 | 8.1729 | 8.3235
Palani 11 | 11.2803 | 12.357 | 11.4046 | 11.1554 | 11.3609
Palani 12 | 239.407 | 262.2596 | 242.047 | 236.7561 | 241.1191
Palani 13 | 0 | 0 | 0 | 0 | 0
Palani 14 | 81.6384 | 89.4312 | 82.5386 | 80.7344 | 82.2222
Panaewa 11 | 129.0156 | 141.3308 | 130.4383 | 127.5871 | 129.9383
Panaewa 12 | 228.9195 | 250.7711 | 231.444 | 226.3848 | 230.5567
Papaaloa 1 | 19.7368 | 21.6207 | 19.9544 | 19.5182 | 19.8779
Papaaloa 2 | 12.8815 | 14.1111 | 13.0236 | 12.7389 | 12.9737
Poopoomino 11 | 182.6523 | 200.0874 | 184.6665 | 180.6299 | 183.9585
Poopoomino 12 | 93.4593 | 102.3804 | 94.4899 | 92.4244 | 94.1276
Poopoomino 13 | 71.8338 | 78.6907 | 72.626 | 71.0384 | 72.3475
Poopoomino 14 | 174.7035 | 191.3798 | 176.63 | 172.7691 | 175.9529
Punaluu 11 | 1.6936 | 1.8553 | 1.7123 | 1.6749 | 1.7057
Punaluu 12 | 18.6933 | 20.4777 | 18.8995 | 18.4864 | 18.827
Puueo 11 | 149.3224 | 163.576 | 150.9691 | 147.669 | 150.3903
Puueo 12 | 153.4301 | 168.0758 | 155.1221 | 151.7313 | 154.5274
Puueo 1402 | 109.7044 | 120.1762 | 110.9141 | 108.4897 | 110.4889
Puuhuluhulu 11 | 70.5636 | 77.2993 | 71.3417 | 69.7823 | 71.0682
Puuhuluhulu 12 | 70.5636 | 77.2993 | 71.3417 | 69.7823 | 71.0682
Puukapu 11 | 147.057 | 161.0944 | 148.6787 | 145.4287 | 148.1087
Puuwaawaa 11 | 100 | 0 | 0 | 0 | 0
Puuwaawaa 12 | 28.6035 | 31.3338 | 28.9189 | 28.2868 | 28.808
Royal Hawaiian | 31.9169 | 34.9635 | 32.2689 | 31.5635 | 32.1452
Shipman 11 | 40.0518 | 43.8749 | 40.4934 | 39.6083 | 40.3382
Shipman 12 | 145.798 | 159.7152 | 147.4058 | 144.1837 | 146.8407
South Point 11 | 830.5608 | 88.2507 | 81.4492 | 79.6688 | 81.1369
South Point 12 | 5.5956 | 6.1297 | 5.6573 | 5.5336 | 5.6356
Umauma 11 | 7.947 | 8.7056 | 8.0346 | 7.859 | 8.0038
Umauma 12 | 13.7396 | 15.0511 | 13.8911 | 13.5875 | 13.8379
Waika 11 | 11.8259 | 12.9548 | 11.9563 | 11.695 | 11.9105
Waika 12 | 210.9684 | 231.1064 | 213.2948 | 208.6324 | 212.4771
Waikii 11 | 44.7225 | 48.9915 | 45.2157 | 44.2273 | 45.0423
Waikii 12 | 21.097 | 23.1108 | 21.3296 | 20.8634 | 21.2478
Waikoloa 11 | 186.1162 | 203.8819 | 188.1686 | 184.0554 | 187.4472
Waikoloa 12 | 466.7244 | 511.2757 | 471.8713 | 461.5566 | 470.0622
Waipunahina 11 | 35.0354 | 38.3797 | 35.4218 | 34.6475 | 35.286
Wright Road 11 | 99.7346 | 109.2548 | 100.8344 | 98.6303 | 100.4478

## Maui Circuit DER Growth
Return to Assumptions Summary
Maui Island Adjusted DER Growth by Circuit - High Forecast
The Adjusted DER Growth by Circuit shows the annual DER growth by circuit. The forecast is shown by circuit (or feeder) peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth (kW)
Circuit | 2021 | 2022 | 2023 | 2024 | 2025
Haiku 16/1358 | 227.4578 | 257.7573 | 251.9145 | 239.9989 | 234.9689
Haiku 16/1361 | 66.0288 | 74.8244 | 73.1283 | 69.6693 | 68.2092
Hana 41/10277 | 7.9693 | 9.0309 | 8.8262 | 8.4087 | 8.2325
Hana 41/537 | 12.8309 | 14.5401 | 14.2105 | 13.5383 | 13.2546
Hana 41/6528 | 4.018 | 4.5532 | 4.45 | 4.2395 | 4.1507
Huelo 74A/Huelo | 16.5228 | 18.7238 | 18.2994 | 17.4338 | 17.0684
Kahului 8/1264 | 90.5294 | 102.5887 | 100.2632 | 95.5208 | 93.5188
Kahului 8/1265 | 263.2497 | 298.317 | 291.5548 | 277.7642 | 271.9427
Kahului 8/4048 | 117.8498 | 133.5485 | 130.5212 | 124.3476 | 121.7414
Kahului 8/4049 | 100.1592 | 113.5013 | 110.9285 | 105.6815 | 103.4666
Kahului 8/4050 | 43.4366 | 49.2227 | 48.107 | 45.8315 | 44.8709
Kailua 9/Kailua | 1.383 | 1.5672 | 1.5317 | 1.4592 | 1.4286
Kanaha 2/1244 | 163.8656 | 185.6941 | 181.4848 | 172.9005 | 169.2768
Kanaha 2/1245 | 110.9289 | 125.7057 | 122.8562 | 117.0451 | 114.592
Kanaha 2/1304 | 175.5232 | 198.9046 | 194.3958 | 185.2009 | 181.3193
Kanaha 2/1305 | 213.0207 | 241.3971 | 235.9251 | 224.7658 | 220.0551
Kanaha 2/1347 | 197.8736 | 224.2322 | 219.1494 | 208.7836 | 204.4078
Kanaha 2/1348 | 62.0569 | 70.3234 | 68.7293 | 65.4784 | 64.1061
Kaonoulu/1590 | 406.7154 | 460.8937 | 450.4462 | 429.14 | 420.1459
Kaonoulu/1591 | 110.0391 | 124.6973 | 121.8707 | 116.1062 | 113.6728
Kauhikoa 98/1295 | 86.1325 | 97.6061 | 95.3936 | 90.8815 | 88.9767
Keanae 42/Keanae | 3.0144 | 3.4159 | 3.3385 | 3.1806 | 3.1139
Kihei 35/1253 | 159.0051 | 180.186 | 176.1016 | 167.772 | 164.2557
Kihei 35/1254 | 350.6276 | 397.3344 | 388.3277 | 369.9598 | 362.206
Kihei 35/1384 | 461.8755 | 523.4016 | 511.5373 | 487.3415 | 477.1275
Kihei 35/1385 | 133.0863 | 150.8146 | 147.396 | 140.4242 | 137.4811
Kihei 35/1473 | 327.8578 | 371.5315 | 363.1097 | 345.9346 | 338.6843
Kihei 35/1515 | 669.708 | 758.9193 | 741.7163 | 706.633 | 691.8231
Kuau 73/4066 | 75.6969 | 85.7804 | 83.836 | 79.8705 | 78.1966
Kuihelani 209/1653 | 450.6226 | 510.6497 | 499.0745 | 475.4681 | 465.5031
Kuihelani 209/1708 | 214.3837 | 242.9416 | 237.4346 | 226.2039 | 221.4631
Kula 13/1237 | 287.4845 | 325.7801 | 318.3954 | 303.3352 | 296.9778
Kula 13/1238 | 289.7797 | 328.3811 | 320.9374 | 305.757 | 299.3488
Kula Ag Park 55/1322 | 53.4215 | 60.5378 | 59.1655 | 56.367 | 55.1856
Lahaina 34/1221 | 210.8505 | 238.9378 | 233.5216 | 222.476 | 217.8132
Lahaina 34/1223 | 295.0512 | 334.3548 | 326.7757 | 311.3192 | 304.7944
Lahaina 34/1225 | 59.477 | 67.3999 | 65.8721 | 62.7563 | 61.441
Lahaina 34/1226 | 33.2892 | 37.7237 | 36.8685 | 35.1247 | 34.3885
Lahaina 34/1390 | 264.9248 | 300.2152 | 293.41 | 279.5316 | 273.6731
Lahaina 34/1397 | 20.7905 | 23.5599 | 23.0259 | 21.9368 | 21.477
Lahaina 34/1398 | 377.9575 | 428.3049 | 418.5962 | 398.7965 | 390.4383
Maalaea 39/1285 | 84.7324 | 96.0195 | 93.843 | 89.4042 | 87.5304
Maalaea 39/1286 | 112.848 | 127.8804 | 124.9816 | 119.07 | 116.5744
Mahinahina 50/1219 | 214.8461 | 243.4656 | 237.9468 | 226.6918 | 221.9407
Mahinahina 50/1380 | 50.8241 | 57.5943 | 56.2888 | 53.6263 | 52.5024
Mahinahina 50/1381 | 1224.807 | 254.7534 | 248.9787 | 237.202 | 232.2306
Makawao 12/1234 | 83.5006 | 94.6237 | 92.4788 | 88.1045 | 86.258
Makawao 12/1235 | 128.6129 | 145.7453 | 142.4416 | 135.7041 | 132.8599
Makawao 12/1236 | 114.615 | 129.8828 | 126.9387 | 120.9345 | 118.3999
Maui Hardwoods 75/522 | 20.5614 | 23.3003 | 22.7722 | 21.6951 | 21.2404
Napili 29/1232 | 52.073 | 59.0096 | 57.672 | 54.9441 | 53.7926
Napili 29/1420 | 917.6947 | 190.0331 | 185.7255 | 176.9407 | 173.2323
Napili 29/1421 | 97.9611 | 111.0104 | 108.4941 | 103.3623 | 101.196
Onehee 40/4055 | 129.225 | 146.4389 | 143.1195 | 136.3499 | 133.4922
Onehee 40/4056 | 52.9985 | 60.0584 | 58.697 | 55.9207 | 54.7486
Paia Mauka 93/4042 | 128.0145 | 145.0672 | 141.7789 | 135.0727 | 132.2418
Peahi 94/1294 | 115.5396 | 130.9306 | 127.9626 | 121.91 | 119.3549
Pukalani 17/1282 | 306.7659 | 347.63 | 339.75 | 323.6798 | 316.8959
Pukalani 17/1283 | 0.6836 | 0.77466 | 0.7571 | 0.72129 | 0.70618
Pukalani 17/1308 | 430.2889 | 487.6073 | 476.5544 | 454.0133 | 444.4978
Pukalani 17/1309 | 45.691 | 51.7775 | 50.6038 | 48.2102 | 47.1998
Puukolii 23/1270 | 558.4493 | 632.8399 | 618.4948 | 589.2399 | 576.8904
Puukolii 23/1271 | 115.8826 | 131.3193 | 128.3425 | 122.2719 | 119.7093
Puukolii 23/1272 | 312.9266 | 354.6113 | 346.5731 | 330.1801 | 323.26
Puukolii 23/1273 | 10.7718 | 12.2067 | 11.93 | 11.3657 | 11.1275
Spreckelsville 92/4043 | 104.8711 | 118.8408 | 116.147 | 110.6532 | 108.3341
Waiehu 43/1378 | 199.1511 | 225.6799 | 220.5642 | 210.1315 | 205.7275
Waiehu 43/1379 | 367.6594 | 416.6351 | 407.1909 | 387.9307 | 379.8003
Waiinu 36/1266 | 110.1902 | 124.8685 | 122.038 | 116.2656 | 113.8289
Waiinu 36/1267 | 59.1303 | 67.007 | 65.4881 | 62.3905 | 61.0829
Waiinu 36/1492 | 100.3186 | 113.6819 | 111.105 | 105.8497 | 103.6313
Waiinu 36/1493 | 821.151 | 930.536 | 909.4428 | 866.426 | 848.267
Waiinu 36/2030 | 31.5859 | 35.7935 | 34.9821 | 33.3274 | 32.6289
Waikapu 77/524 | 0 | 0 | 0 | 0 | 0
Wailea 25/1280 | 280.6128 | 317.9931 | 310.7849 | 296.0847 | 289.8792
Wailea 25/1281 | 69.0862 | 78.2891 | 76.5145 | 72.8953 | 71.3676
Wailea 25/1320 | 244.8943 | 277.5165 | 271.2258 | 258.3967 | 252.9811
Wailea 25/1321 | 3.1392 | 3.5574 | 3.4768 | 3.3123 | 3.2429
Wailea 25/1395 | 48.143 | 54.5561 | 53.3194 | 50.7974 | 49.7328
Wailea 25/1396 | 88.8682 | 100.7063 | 98.4235 | 93.7681 | 91.8028
Wailea 25/1517 | 273.8506 | 310.3301 | 303.2956 | 288.9496 | 282.8937
Wailea 25/1518 | 165.7848 | 187.8689 | 183.6103 | 174.9255 | 171.2594
Wailuku 3/1290 | 442.16 | 501.0599 | 489.7019 | 466.5389 | 456.761
Wailuku 3/1447 | 294.8517 | 334.1287 | 326.5548 | 311.1087 | 304.5883
Wailuku 3/4031 | 56.6947 | 64.247 | 62.7906 | 59.8206 | 58.5669
Wailuku 3/4037 | 88.6894 | 100.5037 | 98.2255 | 93.5794 | 91.6181
Wailuku Heights 18/493 | 87.1141 | 98.7185 | 96.4808 | 91.9173 | 89.9908
Wailuku Heights 18/529 | 55.9232 | 63.3727 | 61.9362 | 59.0066 | 57.7699

## Lanai Circuit DER Growth
Return to Assumptions Summary
Lana‘i Adjusted DER Growth by Circuit - High Forecast
The Adjusted DER Growth by Circuit shows the annual DER growth by circuit. The forecast is shown by circuit (or feeder) peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth (kW)
Circuit | 2021 | 2022 | 2023 | 2024 | 2025
Miki Basin PP 302/1208 | 21.9979 | 24.3977 | 55.1947 | 25.9975 | 56.7946
Miki Basin PP 302/1210 | 7.5723 | 8.3984 | 18.9997 | 8.9491 | 19.5504
Miki Basin PP 302/1212 | 25.4298 | 28.2039 | 63.8056 | 30.0534 | 65.655

## Molokai Circuit DER Growth
Return to Assumptions Summary
Moloka‘i Adjusted DER Growth by Circuit - High Forecast
The Adjusted DER Growth by Circuit shows the annual DER growth by circuit. The forecast is shown by circuit (or feeder) peak in kilowatts (kW) for years 2021-2025.
Adjusted DER Growth (kW)
Circuit | 2021 | 2022 | 2023 | 2024 | 2025
Palaau PP 81/105A | 113.0829 | 115.7673 | 94.6272 | 107.3784 | 83.8894
Palaau PP 81/106B | 30.0353 | 30.7483 | 25.1334 | 28.5202 | 22.2814
Palaau PP 81/109B | 15.3474 | 15.7118 | 12.8427 | 14.5732 | 11.3853
Palaau PP 81/110B | 29.6219 | 30.3251 | 24.7875 | 28.1276 | 21.9747
Palaau PP 81/111A | 370.2114 | 123.0651 | 100.5923 | 114.1473 | 89.1776
Puunana 80/1466 | 4.6554 | 4.7659 | 3.8956 | 4.4205 | 3.4536
Puunana 80/1467 | 22.7239 | 23.2633 | 19.0152 | 21.5776 | 16.8575
Puunana 80/1468 | 1.3218 | 1.3532 | 1.1061 | 1.2551 | 0.98057

## Summary HC Results
Return to Assumptions Summary
Summary of Hosting Capacity Results - High Forecast
These tables summarize the Hosting Capacity Results for all islands.
Island | Total Circuits | Existing Hosting Capacity Satisfies Need (Analysis Not Required) | Forecasted DER > Hosting Capacity (Analysis Required)
O‘ahu | 384 | 303 | 81
Hawai‘i Island | 137 | 76 | 61
Maui Island | 88 | 52 | 36
Lana‘i | 3 | 1 | 2
Moloka‘i | 8 | 3 | 5
Total (All Islands) | 620 | 435 | 185
Island | Grid Needs Not Required |  | Grid Needs Identified
| Existing HC Satisfies Need | Updated HC (w/o Mods) Satisfies Need | Updated HC (w/ Mods) Satisfies Need | Solution Option Required | Total
O‘ahu | 303 | 49 | 15 | 17 | 384
Hawai‘i Island | 76 | 27 | 32 | 2 | 137
Maui Island* | 52 | 16 | 13 | 7 | 88
Lana‘i | 1 | 0 | 0 | 2 | 3
Moloka‘i | 3 | 0 | 0 | 5 | 8
Total (All Islands) | 435 | 92 | 60 | 33 | 620
Figure 7 Data | [5 empty] | Figure 7: Summary of Hosting Capacity Results (% of Total Circuits)
Island | Existing HC Satisfies Need | Updated HC (w/o Mods) Satisfies Need | Updated HC (w/ Mods) Satisfies Need | Solution Option Required | Total
O‘ahu | 78.91% | 12.76% | 3.906% | 4.427% | 100%
Hawai‘i Island | 55.47% | 19.71% | 23.36% | 1.46% | 100%
Maui Island* | 59.09% | 18.18% | 14.77% | 7.955% | 100%
Lana‘i | 33.33% | 0% | 0% | 66.67% | 100%
Moloka‘i | 37.5% | 0% | 0% | 62.5% | 100%
Total (All Islands) | 70.16% | 14.84% | 9.677% | 5.323% | 100%

## Oahu HC Results
Return to Assumptions Summary
O‘ahu Hosting Capacity Analysis Results by Circuit - High Forecast
The Hosting Capacity Analysis Results by Circuit shows the Existing Hosting Capacity (HC) rating compared to the Total 2025 DER Forecast. The Total 2025 DER is the total anticipated DER in year 2025. Circuits with existing hosting capacity able to accommodate the Total 2025 DER are marked with an “X” in the Existing HC Satisfies Need column. Circuits with updated hosting capacity able to accommodate the Total 2025 DER without any modifications are marked with an “X” in the Updated HC (w/o Mods) Satisfies Need column. Circuits with updated hosting capacity and modifications (non-infrastructure investment solutions) able to accommodate the Total 2025 DER are marked with an “X” in the Updated HC (w/ Mods) Satisfies Needs column. Circuits that require infrastructure investment solutions are marked with an "X" in the Solution Option Required column. Additional details for these circuits are shown in the Grid Needs Assessment (GNA) tables. The Circuit Count provides a summary of the hosting caapcity results. The Hosting Capacity Increase (kW) is an estimate of the increase in hosting capacity due to the total updated hosting capacity available for all circuits as a result of this analysis. The Total 2025 DER forecast and hosting capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
Circuit Name | Total 2025 DER (kW) | Existing HC (kW) | Existing HC Satisfies Need | Updated HC (kW) | Updated HC (w/o Mods) Satisfies Need | Updated HC (w/ Mods) Satisfies Need | Solution Option Required | HC Increase (kW) | Circuit Count | Total
AALA | 1990.014 | 6044 | x |  |  |  |  | 0 | Total Circuits | 384
AALAPAPA | 4265.811 | 4786 | x |  |  |  |  | 0 | Existing HC Satisfies Need | 303
AHUA | 1972.899 | 1561 |  | 6080 | x |  |  | 411.899 | Updated HC (w/o Modifications) | 49
AHUI | 0 | 361 | x |  |  |  |  | 0 | Updated HC (w Modifications) | 15
AIEA | 4563.117 | 3601 |  | 5700 |  | x |  | 962.117 | Solution Option Required | 17
AIEA 2 | 636.094 | 2986 | x |  |  |  |  | 0
AIEA 3 | 571.241 | 1008 | x |  |  |  |  | 0
AINA KOA | 4628.381 | 2951 |  | 4926 |  |  | x | 1677.381
AINONI | 1477.228 | 1500 | x |  |  |  |  | 0 | Hosting Capacity Increase (kW) | 64730.332
AIRPORT | 3076.158 | 5669 | x |  |  |  |  | 0
AIRPORT 1 | 100 | 2724 | x |  |  |  |  | 0
AIRPORT 2 | 100 | 1716 | x |  |  |  |  | 0
ALA MOANA | 354.147 | 6272 | x |  |  |  |  | 0
ALEWA | 561.74 | 580 | x |  |  |  |  | 0
ALIAMANU | 5189.681 | 6346 | x |  |  |  |  | 0
ANOI | 4854.073 | 3794 |  | 6360 | x |  |  | 1060.073
ANUU | 4993.407 | 4073 |  | 5321.2 |  | x |  | 920.407
ARCHER 1 | 400 | 2402 | x |  |  |  |  | 0
ARCHER 2 | 305.956 | 3003 | x |  |  |  |  | 0
ARCHER 3 | 2158.417 | 7277 | x |  |  |  |  | 0
ARCHER 4 | 278 | 5293 | x |  |  |  |  | 0
AUDITORIUM | 894.36 | 4589 | x |  |  |  |  | 0
BARBERS PT | 1930.77 | 7170 | x |  |  |  |  | 0
BAY DR | 1274.331 | 1424 | x |  |  |  |  | 0
BEACH LOTS | 4979.795 | 4712 |  | 6500 | x |  |  | 267.795
BECKLEY | 299.315 | 304 | x |  |  |  |  | 0
BLACK PT | 734.44 | 1007 | x |  |  |  |  | 0
BWS | 1376.163 | 4190 | x |  |  |  |  | 0
CARLOS LONG | 3816.164 | 3984 | x |  |  |  |  | 0
CASTNER | 2170.224 | 6569 | x |  |  |  |  | 0
CEIP 3 | 3138.234 | 6243 | x |  |  |  |  | 0
CEIP 4 | 926.923 | 1478 | x |  |  |  |  | 0
CKT 10 | 430.75 | 2068 | x |  |  |  |  | 0
CKT 12 | 200 | 3107 | x |  |  |  |  | 0
CKT 16 | 7991.921 | 6611 |  | 10012 | x |  |  | 1380.921
CKT 18 | 1492.469 | 4151 | x |  |  |  |  | 0
CKT 6 | 828.35 | 2806 | x |  |  |  |  | 0
CKT 7 | 1425.573 | 4397 | x |  |  |  |  | 0
CKT 8 | 100 | 1403 | x |  |  |  |  | 0
COCONUT GROVE | 1449.729 | 1457 | x |  |  |  |  | 0
DAIRYMENS | 654.465 | 2649 | x |  |  |  |  | 0
DE RUSSY | 200 | 3126 | x |  |  |  |  | 0
DEPOT RD | 1672.71 | 2327 | x |  |  |  |  | 0
DIAMOND HEAD | 2709.38 | 1452 |  | 3280 |  | x |  | 1257.38
DOLE 1 | 2712.621 | 5673 | x |  |  |  |  | 0
EKEKELA | 1096.058 | 1070 |  | 1312 | x |  |  | 26.058
ENA 1 | 402.934 | 3559 | x |  |  |  |  | 0
ENA 2 | 0 | 4529 | x |  |  |  |  | 0
ENCHANTED LAKES | 4723.748 | 5155 | x |  |  |  |  | 0
EWA BEACH 1 | 5791.611 | 6550 | x |  |  |  |  | 0
EWA BEACH 2 | 4250.829 | 4257 | x |  |  |  |  | 0
EWA BEACH 3 | 4998.736 | 4029 |  | 4999 |  | x |  | 969.736
EWA BEACH 4 | 8045.949 | 5966 |  | 8046 |  | x |  | 2079.949
EWA NUI 1 | 4689.348 | 6430 | x |  |  |  |  | 0
EWA NUI 2 | 8088.111 | 6024 |  | 8089 | x |  |  | 2064.111
FARMERS RD | 1746.258 | 1411 |  | 1746.26 |  |  | x | 335.258
FORT ST | 728.263 | 4340 | x |  |  |  |  | 0
FORT ST 1 | 303.66 | 3014 | x |  |  |  |  | 0
FORT ST 2 | 462.957 | 3672 | x |  |  |  |  | 0
FORT ST 3 | 486.82 | 3667 | x |  |  |  |  | 0
FORT ST 4 | 1089.71 | 2895 | x |  |  |  |  | 0
FORT WEAVER 1 | 5279.348 | 5458 | x |  |  |  |  | 0
FORT WEAVER 2 | 7051.215 | 6321 |  | 7052 | x |  |  | 730.215
FORT WEAVER 3 | 6589.204 | 5950 |  | 6590 | x |  |  | 639.204
FORT WEAVER 4 | 3181.406 | 4293 | x |  |  |  |  | 0
HAHAIONE | 3453.905 | 3366 |  | 3964.8 | x |  |  | 87.905
HALA 1 | 2958.867 | 4003 | x |  |  |  |  | 0
HALA 2 | 2365.535 | 4308 | x |  |  |  |  | 0
HALA 3 | 3617.674 | 4824 | x |  |  |  |  | 0
HALA 4 | 2047.867 | 4351 | x |  |  |  |  | 0
HALAWA | 3727.592 | 6775 | x |  |  |  |  | 0
HALEKOU | 4524.857 | 5289 | x |  |  |  |  | 0
HANUA 1 | 0 | 0 | x |  |  |  |  | 0
HANUA 2 | 0 | 0 | x |  |  |  |  | 0
HAUULA | 7142.088 | 2802 |  | 8630 | x |  |  | 4340.088
HAWN PINE | 1618 | 5841 | x |  |  |  |  | 0
HAWN VILLAGE 1 | 206.312 | 3528 | x |  |  |  |  | 0
HAWN VILLAGE 2 | 546.499 | 2673 | x |  |  |  |  | 0
HEEIA | 5006.076 | 5140 | x |  |  |  |  | 0
HEIGHTS | 1397.452 | 1145 |  | 1397.5 | x |  |  | 252.452
HELEMANO | 3299.047 | 4406 | x |  |  |  |  | 0
HIGHLANDS | 5523.309 | 6162 | x |  |  |  |  | 0
HIKINA | 253.924 | 220 |  | 491.8 | x |  |  | 33.924
HILA 1 | 1646.596 | 1968 | x |  |  |  |  | 0
HILA 2 | 2637.77 | 3688 | x |  |  |  |  | 0
HILA 3 | 2089.896 | 5288 | x |  |  |  |  | 0
HILA 4 | 400 | 0 |  | 2323 | x |  |  | 400
HILA 5 | 2347.11 | 6597 | x |  |  |  |  | 0
HILA 6 | 0 | 0 | x |  |  |  |  | 0
HOAEAE 1 | 6504.755 | 5113 |  | 8445 | x |  |  | 1391.755
HOAEAE 2 | 1379.325 | 2163 | x |  |  |  |  | 0
HOAEAE 3 | 4037.225 | 2488 |  | 4038 | x |  |  | 1549.225
HOUGHTAILING | 1414.758 | 5510 | x |  |  |  |  | 0
HUNAKAI | 1011.796 | 1508 | x |  |  |  |  | 0
ILANIWAI | 396.219 | 3605 | x |  |  |  |  | 0
ILIAINA | 2121.679 | 2541 | x |  |  |  |  | 0
ILIKAI | 398.063 | 4283 | x |  |  |  |  | 0
INDUSTRIAL | 4119.617 | 7546 | x |  |  |  |  | 0
IWILEI 1 11KV | 2137.185 | 7190 | x |  |  |  |  | 0
IWILEI 13 | 369.58 | 3979 | x |  |  |  |  | 0
IWILEI 9 | 0 | 4164 | x |  |  |  |  | 0
KAALAKEI | 4521.7 | 5132 | x |  |  |  |  | 0
KAENA PT | 3328.799 | 2739 |  | 3328.8 |  | x |  | 589.799
KAHAI | 3504.402 | 6866 | x |  |  |  |  | 0
KAHALA | 2591.055 | 1976 |  | 2591.06 |  |  | x | 615.055
KAHALA 3 | 7171.717 | 1609 |  | 7269 | x |  |  | 5562.717
KAHALA MALL | 2729.756 | 2970 | x |  |  |  |  | 0
KAHALOA | 1502.763 | 1407 |  | 1630 | x |  |  | 95.763
KAHE | 3781.826 | 5684 | x |  |  |  |  | 0
KAHUKU | 3363.156 | 2422 |  | 4240 | x |  |  | 941.156
KAI-HARDING | 482.05 | 471 |  | 483 | x |  |  | 11.05
KAI-KAIMUKI | 875.687 | 1162 | x |  |  |  |  | 0
KAILUA 1 | 4008.813 | 3746 |  | 5341.3 | x |  |  | 262.813
KAILUA 2 | 6362.057 | 7039 | x |  |  |  |  | 0
KAILUA HTS | 5946.756 | 5755 |  | 6120 |  | x |  | 191.756
KAINALU | 2598.058 | 1047 |  | 2625.3 |  |  | x | 1551.058
KAI-WAIALAE | 1265.089 | 1646 | x |  |  |  |  | 0
KAI-WILHELMINA | 696.695 | 930 | x |  |  |  |  | 0
KAKAAKO 5 | 155.087 | 430 | x |  |  |  |  | 0
KAKAAKO 6 | 200 | 1646 | x |  |  |  |  | 0
KAKAAKO 8 | 1250.13 | 3781 | x |  |  |  |  | 0
KAKAAKO 9 | 1165.167 | 7502 | x |  |  |  |  | 0
KALAHEO | 1637.376 | 1462 |  | 1800 |  | x |  | 175.376
KALAHEO 1 | 441 | 2344 | x |  |  |  |  | 0
KALAHEO 2 | 0 | 0 | x |  |  |  |  | 0
KALAKAUA | 502.718 | 4831 | x |  |  |  |  | 0
KALAMA | 1086.792 | 1277 | x |  |  |  |  | 0
KALIA | 0 | 5654 | x |  |  |  |  | 0
KALIHI | 336.932 | 5187 | x |  |  |  |  | 0
KALIHI KAI | 891.022 | 1604 | x |  |  |  |  | 0
KALIHI ST | 1097.737 | 1021 |  | 1620 | x |  |  | 76.737
KALIHI UKA | 561.474 | 1278 | x |  |  |  |  | 0
KALIHI VALLEY | 947.233 | 1701 | x |  |  |  |  | 0
KALOI 1 | 1314.56 | 612 |  | 2979 | x |  |  | 702.56
KAM HWY | 1431.664 | 5123 | x |  |  |  |  | 0
KAM IV | 1299.527 | 1322 | x |  |  |  |  | 0
KAM TERRACE | 1934.804 | 1323 |  | 3800 | x |  |  | 611.804
KAMAKEE | 371.216 | 2456 | x |  |  |  |  | 0
KAMANI | 266.26 | 1505 | x |  |  |  |  | 0
KAMOKILA 1 | 2563.355 | 4660 | x |  |  |  |  | 0
KAMOKILA 2 | 3232.984 | 4541 | x |  |  |  |  | 0
KAMOKILA 3 | 2820.534 | 2937 | x |  |  |  |  | 0
KAMOKILA 4 | 3913.25 | 3966 | x |  |  |  |  | 0
KAMOKILA 5 | 2481.6 | 6548 | x |  |  |  |  | 0
KAMOKILA 6 | 1935.561 | 3259 | x |  |  |  |  | 0
KAMOKU 10 | 506.78 | 8363 | x |  |  |  |  | 0
KAMOKU 9 | 240.56 | 6223 | x |  |  |  |  | 0
KANAINA | 4370.083 | 6528 | x |  |  |  |  | 0
KANEKAPOLEI | 1063.633 | 3308 | x |  |  |  |  | 0
KANEOHE 5 | 2603.831 | 2804 | x |  |  |  |  | 0
KANEOHE 6 | 2178.438 | 5977 | x |  |  |  |  | 0
KAONOHI 1 | 1641.58 | 3482 | x |  |  |  |  | 0
KAONOHI 2 | 4381.659 | 5066 | x |  |  |  |  | 0
KAONOHI 3 | 1018.347 | 4965 | x |  |  |  |  | 0
KAONOHI 4 | 826.545 | 4030 | x |  |  |  |  | 0
KAPAHULU 1 | 205.066 | 1355 | x |  |  |  |  | 0
KAPAHULU 2 | 0 | 5774 | x |  |  |  |  | 0
KAPAHULU 3 | 211.74 | 4879 | x |  |  |  |  | 0
KAPAHULU 4 | 169.857 | 3629 | x |  |  |  |  | 0
KAPALAMA | 401.575 | 587 | x |  |  |  |  | 0
KAP-HARDING | 1025.141 | 1157 | x |  |  |  |  | 0
KAPIOLANI 1 | 1896.058 | 4867 | x |  |  |  |  | 0
KAPIOLANI 2 | 2236.548 | 5354 | x |  |  |  |  | 0
KAPIOLANI 3 | 2090.492 | 4056 | x |  |  |  |  | 0
KAP-KAIMUKI | 389.928 | 1911 | x |  |  |  |  | 0
KAPOLEI 1 | 105.52 | 644 | x |  |  |  |  | 0
KAPOLEI 2 | 2923.036 | 4169 | x |  |  |  |  | 0
KAPOLEI 3 | 1361.081 | 3780 | x |  |  |  |  | 0
KAPOLEI 4 | 6970.09 | 2966 |  | 6971 | x |  |  | 4004.09
KAP-WAIALAE | 1014.723 | 1032 | x |  |  |  |  | 0
KAUHALE | 1697.986 | 6157 | x |  |  |  |  | 0
KAWAILOA | 1920.292 | 1133 |  | 2467.5 |  | x |  | 787.292
KAWELA | 3546.383 | 4800 | x |  |  |  |  | 0
KEALAOLU | 505.639 | 1120 | x |  |  |  |  | 0
KEAWE | 1021.61 | 4502 | x |  |  |  |  | 0
KEEHI 1 | 617.895 | 2912 | x |  |  |  |  | 0
KEEHI 5 | 1881.7 | 3166 | x |  |  |  |  | 0
KEEHI 6 | 1357.679 | 4074 | x |  |  |  |  | 0
KEEHI 7 | 929.9 | 2866 | x |  |  |  |  | 0
KEEHI 8 | 400 | 1766 | x |  |  |  |  | 0
KEOLU DR | 3013.49 | 4497 | x |  |  |  |  | 0
KEWALO | 7888.251 | 7024 |  | 11692 | x |  |  | 864.251
KEWALO 1 | 372.356 | 3591 | x |  |  |  |  | 0
KEWALO 2 | 319.864 | 4809 | x |  |  |  |  | 0
KEWALO 3 | 0 | 73 | x |  |  |  |  | 0
KEWALO 4 | 578.923 | 2953 | x |  |  |  |  | 0
KEWALO 5 | 500 | 11185 | x |  |  |  |  | 0
KEWALO 6 | 370 | 5907 | x |  |  |  |  | 0
KEWALO 7 | 0 | 0 | x |  |  |  |  | 0
KILAUEA 12KV | 2406.47 | 6299 | x |  |  |  |  | 0
KILAUEA 4KV | 1231.076 | 962 |  | 1330 |  |  | x | 269.076
KIPAPA | 1325.355 | 3487 | x |  |  |  |  | 0
KO OLINA 1 | 715.639 | 8395 | x |  |  |  |  | 0
KO OLINA 2 | 0 | 84 | x |  |  |  |  | 0
KO OLINA 3 | 500 | 4546 | x |  |  |  |  | 0
KOKOHEAD | 2983.683 | 3252 | x |  |  |  |  | 0
KOLOA | 1594.945 | 1281 |  | 1594.95 |  |  | x | 313.945
KONA ST | 0 | 893 | x |  |  |  |  | 0
KUAHELANI 1 | 3206.952 | 4897 | x |  |  |  |  | 0
KUAHELANI 2 | 2205.761 | 4138 | x |  |  |  |  | 0
KUAHELANI 3 | 4304.203 | 7671 | x |  |  |  |  | 0
KUAHELANI 4 | 6684.546 | 10634 | x |  |  |  |  | 0
KUAKINI | 195.77 | 952 | x |  |  |  |  | 0
KUAPA 1 | 2709.022 | 4410 | x |  |  |  |  | 0
KUAPA 2 | 2364.274 | 1891 |  | 6740 | x |  |  | 473.274
KUAPA 3 | 3528.109 | 4110 | x |  |  |  |  | 0
KUAPA 4 | 2851.464 | 3136 | x |  |  |  |  | 0
KUHIO | 208.007 | 505 | x |  |  |  |  | 0
KUHIO 1 | 224.653 | 5370 | x |  |  |  |  | 0
KUHIO 2 | 600 | 983 | x |  |  |  |  | 0
KUHIO 3 | 107.32 | 3562 | x |  |  |  |  | 0
KUHIO 4 | 697.35 | 3627 | x |  |  |  |  | 0
KUILIMA 1 | 1605.071 | 1524 |  | 1605.08 |  | x |  | 81.071
KUNIA | 833.545 | 1711 | x |  |  |  |  | 0
KUNIA MAKAI 1 | 2674.464 | 3433 | x |  |  |  |  | 0
KUNIA MAKAI 2 | 6695.201 | 7394 | x |  |  |  |  | 0
KUNIA MAKAI 3 | 4828.225 | 5979 | x |  |  |  |  | 0
KUNIA MAKAI 4 | 1855.004 | 2007 | x |  |  |  |  | 0
LAGOON | 1400.172 | 8176 | x |  |  |  |  | 0
LAKESIDE 1 | 3982.508 | 4373 | x |  |  |  |  | 0
LAKESIDE 2 | 1172.658 | 2008 | x |  |  |  |  | 0
LAKESIDE 3 | 2090.025 | 5447 | x |  |  |  |  | 0
LAKESIDE 4 | 2539.673 | 3541 | x |  |  |  |  | 0
LANIKAI | 3.879 | 179 | x |  |  |  |  | 0
LAULIMA | 3161.757 | 4187 | x |  |  |  |  | 0
LEAHI | 3585.684 | 5460 | x |  |  |  |  | 0
LEOMELE | 2853.353 | 2938 | x |  |  |  |  | 0
LEOOLE | 2884.661 | 3527 | x |  |  |  |  | 0
LIBERTY HOUSE | 194.94 | 2502 | x |  |  |  |  | 0
LIGHTHOUSE | 1637.945 | 7972 | x |  |  |  |  | 0
LIKELIKE | 603.305 | 680 | x |  |  |  |  | 0
LILIHA MAKAI | 98.016 | 190 | x |  |  |  |  | 0
LOWREY | 1359.511 | 1129 |  | 1380 |  |  | x | 230.511
LUAWAI | 4165.899 | 7351 | x |  |  |  |  | 0
LUMIAUAU | 2331.775 | 4579 | x |  |  |  |  | 0
MACHADO ST | 854.629 | 736 |  | 1500 | x |  |  | 118.629
MAHUKONA | 1420.99 | 4899 | x |  |  |  |  | 0
MAKAHA | 4959.684 | 5685 | x |  |  |  |  | 0
MAKAHA VALLEY | 1829.603 | 1725 |  | 1830 | x |  |  | 104.603
MAKAKILO 1 | 4336.67 | 3988 |  | 4539 | x |  |  | 348.67
MAKAKILO 2 | 10569.553 | 8472 |  | 10570 |  | x |  | 2097.553
MAKAKILO 3 | 4436.513 | 5277 | x |  |  |  |  | 0
MAKAKILO 4 | 1516.117 | 1813 | x |  |  |  |  | 0
MAKALAPA-MOANALUA | 3261.719 | 4285 | x |  |  |  |  | 0
MAKALOA | 614.601 | 4602 | x |  |  |  |  | 0
MALAKOLE | 0 | 0 | x |  |  |  |  | 0
MALAKOLE 4 | 5915.954 | 6087 | x |  |  |  |  | 0
MANAGERS | 968.941 | 1478 | x |  |  |  |  | 0
MANOA 1 | 2388.882 | 2732 | x |  |  |  |  | 0
MANOA 2 | 1228.589 | 1089 |  | 2180 | x |  |  | 139.589
MANOA 3 | 3161.999 | 4168 | x |  |  |  |  | 0
MANOA 4 | 0 | 266 | x |  |  |  |  | 0
MANOA-MCCULLY | 479.852 | 4259 | x |  |  |  |  | 0
MANOA-PIIKOI | 1963.032 | 1553 |  | 2090 |  |  | x | 410.032
MAPUNAPUNA | 1077.78 | 371 |  | 3835 | x |  |  | 706.78
MAPUNAPUNA-MOANALUA | 2225.714 | 2345 | x |  |  |  |  | 0
MAUKA | 10282.251 | 8350 |  | 10283 |  |  | x | 1932.251
MAUNALANI | 2121.762 | 2057 |  | 2159 | x |  |  | 64.762
MAUNAWILI | 0 | 108 | x |  |  |  |  | 0
MCCULLY 1 | 1796.404 | 7195 | x |  |  |  |  | 0
MCCULLY 3 | 2027.047 | 5548 | x |  |  |  |  | 0
MCCULLY 5 | 1075.492 | 3836 | x |  |  |  |  | 0
MIKILUA 1 | 2637.034 | 6431 | x |  |  |  |  | 0
MIKILUA 3 | 5439.32 | 4761 |  | 5440 |  |  | x | 678.32
MIKILUA 4 | 7652.835 | 3514 |  | 7653 |  |  | x | 4138.835
MIKILUA 5 | 8544.115 | 7382 |  | 8545 |  |  | x | 1162.115
MILILANI 1 | 3273.991 | 4605 | x |  |  |  |  | 0
MILILANI 2 | 2316.378 | 5475 | x |  |  |  |  | 0
MILILANI 3 | 2400.53 | 3763 | x |  |  |  |  | 0
MILILANI 4 | 6662.182 | 7449 | x |  |  |  |  | 0
MOILIILI 1 | 2007.496 | 4596 | x |  |  |  |  | 0
MOILIILI 2 | 1197.145 | 3937 | x |  |  |  |  | 0
MOKAUEA | 487.518 | 2933 | x |  |  |  |  | 0
MOKUOLA | 3848.227 | 6033 | x |  |  |  |  | 0
MOKUONE 1 | 0 | 4641 | x |  |  |  |  | 0
MOKUONE 2 | 1370.56 | 4421 | x |  |  |  |  | 0
NIU | 3617.46 | 4171 | x |  |  |  |  | 0
NUMANA | 524.354 | 1154 | x |  |  |  |  | 0
NUUANU | 978.188 | 719 |  | 2160 | x |  |  | 259.188
NUUANU 2 | 2734.333 | 5155 | x |  |  |  |  | 0
NUUANU 3 | 4340.915 | 6965 | x |  |  |  |  | 0
OCEAN POINTE 1 | 6063.05 | 5876 |  | 6064 | x |  |  | 187.05
OCEAN POINTE 2 | 5453.231 | 5280 |  | 5454 | x |  |  | 173.231
OCEAN POINTE 3 | 4383.821 | 5444 | x |  |  |  |  | 0
OCEAN POINTE 4 | 1712.819 | 1362 |  | 1713 | x |  |  | 350.819
OLOMANA | 2030.232 | 2936 | x |  |  |  |  | 0
ONEAWA | 1178.436 | 908 |  | 2160 |  | x |  | 270.436
PAHIA | 2309.315 | 1505 |  | 4310 | x |  |  | 804.315
PAIWA | 1986.2 | 3378 | x |  |  |  |  | 0
PALEKA | 2362.802 | 2584 | x |  |  |  |  | 0
PALI | 3908.966 | 4764 | x |  |  |  |  | 0
PAOAKALANI | 1767.996 | 5271 | x |  |  |  |  | 0
PAUOA 1 | 2197.555 | 2333 | x |  |  |  |  | 0
PAUOA 2 | 5391.719 | 4522 |  | 7130 |  |  | x | 869.719
PAWAA KAI | 1060.704 | 2667 | x |  |  |  |  | 0
PAWAINA | 1770.995 | 1824 | x |  |  |  |  | 0
PEARL CITY 1 | 2723.079 | 5934 | x |  |  |  |  | 0
PEARL CITY 2 | 3161.509 | 5588 | x |  |  |  |  | 0
PENINSULA | 2770.004 | 6106 | x |  |  |  |  | 0
PENSACOLA | 1663.693 | 3860 | x |  |  |  |  | 0
PIIKOI | 989.697 | 4017 | x |  |  |  |  | 0
PIIKOI 7 | 938.795 | 2773 | x |  |  |  |  | 0
PIIKOI 8 | 2719.564 | 1993 |  | 3469 |  |  | x | 726.564
POAMOHO | 0 | 0 | x |  |  |  |  | 0
POHAKUPU 4 | 4012.538 | 4054 | x |  |  |  |  | 0
PORTLOCK | 5120.007 | 4113 |  | 5580 |  | x |  | 1007.007
PUNALUU | 3448.761 | 3552 | x |  |  |  |  | 0
PUNCHBOWL | 883.877 | 656 |  | 1240 | x |  |  | 227.877
PUOHALA 1 | 2635.902 | 4019 | x |  |  |  |  | 0
PUOHALA 2 | 6571.53 | 7179 | x |  |  |  |  | 0
PUUHALE | 1729.011 | 2526 | x |  |  |  |  | 0
PUUNUI | 1347.534 | 1354 | x |  |  |  |  | 0
QUEEN ST | 375.024 | 2128 | x |  |  |  |  | 0
QUEENS 1 | 3259.56 | 3735 | x |  |  |  |  | 0
QUEENS 2 | 1732.816 | 1722 |  | 1732.82 | x |  |  | 10.816
RUGER | 587.533 | 1010 | x |  |  |  |  | 0
SAND ISLAND | 1058.649 | 6808 | x |  |  |  |  | 0
SAND ISLAND 1 | 460 | 6285 | x |  |  |  |  | 0
SAND ISLAND 2 | 463 | 3034 | x |  |  |  |  | 0
SCHOOL ST | 2529.131 | 3452 | x |  |  |  |  | 0
SCHOOL ST 3 | 2047.836 | 5183 | x |  |  |  |  | 0
SHAFTER | 1022.4 | 3086 | x |  |  |  |  | 0
SHERATON 1 | 284.426 | 1536 | x |  |  |  |  | 0
SHERATON 2 | 48.104 | 4551 | x |  |  |  |  | 0
SHOPPING CTR | 1406.04 | 4165 | x |  |  |  |  | 0
SOUTH RAMP 1 | 2274.39 | 3765 | x |  |  |  |  | 0
ST LOUIS | 2538.763 | 2853 | x |  |  |  |  | 0
ST LOUIS HTS | 161.476 | 337 | x |  |  |  |  | 0
THURSTON | 1749.534 | 4669 | x |  |  |  |  | 0
TOWN | 8.921 | 144 | x |  |  |  |  | 0
UALENA | 1757.588 | 5228 | x |  |  |  |  | 0
UPLANDS | 1377.235 | 1379 | x |  |  |  |  | 0
UWAPO 1 | 5028.784 | 5433 | x |  |  |  |  | 0
UWAPO 2 | 1618.477 | 1637 | x |  |  |  |  | 0
UWAPO 3 | 5098.38 | 5881 | x |  |  |  |  | 0
UWAPO 4 | 38.04 | 924 | x |  |  |  |  | 0
WAHIAWA HTS | 4428.387 | 4206 |  | 4428.39 | x |  |  | 222.387
WAHIAWA PROPER | 1629.821 | 5964 | x |  |  |  |  | 0
WAIAKAMILO 1 | 698.08 | 2530 | x |  |  |  |  | 0
WAIAKAMILO 2 | 1069.13 | 5490 | x |  |  |  |  | 0
WAIAKAMILO 3 | 2866.837 | 5827 | x |  |  |  |  | 0
WAIAKAMILO 4 | 1715.343 | 3697 | x |  |  |  |  | 0
WAIAKAMILO-IWILEI | 852.72 | 959 | x |  |  |  |  | 0
WAIAKAMILO-KAPALAMA | 2892.494 | 9020 | x |  |  |  |  | 0
WAIALAE NUI | 2436.644 | 3646 | x |  |  |  |  | 0
WAIALAE SC | 0 | 746 | x |  |  |  |  | 0
WAIALUA | 2641.675 | 1711 |  | 3301.7 |  | x |  | 930.675
WAIAWA 1 | 4683.198 | 6447 | x |  |  |  |  | 0
WAIAWA 2 | 3294.931 | 9144 | x |  |  |  |  | 0
WAIAWA 3 | 3492.73 | 7605 | x |  |  |  |  | 0
WAIAWA 4 | 2819.441 | 4257 | x |  |  |  |  | 0
WAIHEE 1 | 3704.643 | 3804 | x |  |  |  |  | 0
WAIHEE 2 | 2419.175 | 2101 |  | 2419.18 | x |  |  | 318.175
WAIHEE 3 | 887.709 | 660 |  | 887.71 | x |  |  | 227.709
WAIHEE 4 | 4279.849 | 4189 |  | 4279.85 | x |  |  | 90.849
WAIKELE CTR | 1036.524 | 3133 | x |  |  |  |  | 0
WAIKIKI 1 | 362.353 | 1844 | x |  |  |  |  | 0
WAIKIKI 2 | 200 | 6144 | x |  |  |  |  | 0
WAIKIKI 3 | 494.638 | 6602 | x |  |  |  |  | 0
WAIKIKI 4 | 494.372 | 6104 | x |  |  |  |  | 0
WAIKIKI 5 | 1170.351 | 3888 | x |  |  |  |  | 0
WAIKIKI 6 | 600 | 4256 | x |  |  |  |  | 0
WAILANI | 1725.009 | 2982 | x |  |  |  |  | 0
WAILUPE | 8165.261 | 6579 |  | 8653 |  |  | x | 1586.261
WAIMALU 1 | 3937.832 | 6268 | x |  |  |  |  | 0
WAIMALU 2 | 3430.961 | 4994 | x |  |  |  |  | 0
WAIMALU 3 | 6430.662 | 5984 |  | 6430.664 | x |  |  | 446.662
WAIMALU 4 | 2647.765 | 3523 | x |  |  |  |  | 0
WAIMANALO | 2320.401 | 2248 |  | 2480 |  |  | x | 72.401
WAIMANO 5 | 2180.37 | 2078 |  | 2180.37 | x |  |  | 102.37
WAIMANO 6 | 2644.995 | 4506 | x |  |  |  |  | 0
WAIMANO HOME RD | 5554.959 | 5099 |  | 5554.96 | x |  |  | 455.959
WAIMEA 1 | 701.496 | 788 | x |  |  |  |  | 0
WAIMEA 2 | 3396.283 | 3168 |  | 3495 |  | x |  | 228.283
WAIOMAO | 5061.406 | 5743 | x |  |  |  |  | 0
WAIPAHU | 10233.366 | 8874 |  | 10233.4 | x |  |  | 1359.366
WAIPIO 1 | 1782.73 | 4249 | x |  |  |  |  | 0
WAIPIO 2 | 1238.635 | 4040 | x |  |  |  |  | 0
WAIWAI | 1147.01 | 2823 | x |  |  |  |  | 0
WAI-WILHELMINA | 1456.392 | 1376 |  | 1480 |  |  | x | 80.392
WHITMORE | 79.414 | 308 | x |  |  |  |  | 0
WILIWILI | 2426.617 | 2293 |  | 4090 | x |  |  | 133.617
WILIWILI 2 | 2563.058 | 2126 |  | 2566 | x |  |  | 437.058
WOODLAWN | 1207.314 | 1242 | x |  |  |  |  | 0

## Hawaii Island HC Results
Return to Assumptions Summary
Hawai‘i Island Hosting Capacity Analysis Results by Circuit - High Forecast
The Hosting Capacity Analysis Results by Circuit shows the Existing Hosting Capacity (HC) rating compared to the Total 2025 DER Forecast. The Total 2025 DER is the total anticipated DER in year 2025. Circuits with existing hosting capacity able to accommodate the Total 2025 DER are marked with an “X” in the Existing HC Satisfies Need column. Circuits with updated hosting capacity able to accommodate the Total 2025 DER without any modifications are marked with an “X” in the Updated HC (w/o Mods) Satisfies Need column. Circuits with updated hosting capacity and modifications (non-infrastructure investment solutions) able to accommodate the Total 2025 DER are marked with an “X” in the Updated HC (w/ Mods) Satisfies Needs column. Circuits that require infrastructure investment solutions are marked with an "X" in the Solution Option Required column. Additional details for these circuits are shown in the Grid Needs Assessment (GNA) tables. The Circuit Count provides a summary of the hosting caapcity results. The Hosting Capacity Increase (kW) is an estimate of the increase in hosting capacity due to the total updated hosting capacity available for all circuits as a result of this analysis. The Total 2025 DER forecast and hosting capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
Circuit Name | Total 2025 DER (kW) | Existing HC (kW) | Existing HC Satisfies Need | Updated HC (kW) | Updated HC (w/o Mods) Satisfies Need | Updated HC (w/ Mods) Satisfies Need | Solution Option Required | HC Increase (kW) | Circuit Count | Total
Ainaloa 11 | 1163.6851 | 1722 | x |  |  |  |  | 0 | Total Circuits | 137
Ainaloa 12 | 818.8313 | 1319 | x |  |  |  |  | 0 | Existing HC Satisfies Need | 76
Anaehoomalu 11 | 292.8154 | 1411.1 | x |  |  |  |  | 0 | Updated HC (w/o Modifications) | 27
Anaehoomalu 12 | 499.0761 | 2083.4475 | x |  |  |  |  | 0 | Updated HC (w Modifications) | 32
Anaehoomalu 13 | 355.5078 | 4099.1687 | x |  |  |  |  | 0 | Solution Option Required | 2
Captain Cook 11 | 2451.6476 | 3876 | x |  |  |  |  | 0
Captain Cook 12 | 1873.5347 | 1795 |  | 7000 |  | x |  | 78.5347
Hakalau 1 | 269.933 | 319 | x |  |  |  |  | 0
Halaula 1 | 980.4225 | 743 |  | 1375 |  |  | x | 237.4225 | Hosting Capacity Increase (kW) | 37832.1677
Halaula 2 | 0 | 0 | x |  |  |  |  | 0
Hale Pohaku 11 | 389.5551 | 85 |  | 3730 | x |  |  | 304.5551
Hale Pohaku 12 | 164.3318 | 83 |  | 2370 | x |  |  | 81.3318
Haleaha 11 | 792.1361 | 2624.657 | x |  |  |  |  | 0
Haleaha 12 | 2456.7668 | 4433 | x |  |  |  |  | 0
Hawaiian Beaches 11 | 1249.8144 | 2129 | x |  |  |  |  | 0
Hawaiian Beaches 12 | 9.2133 | 127 | x |  |  |  |  | 0
Hawaiian Paradise Park 11 | 1173.2419 | 3346 | x |  |  |  |  | 0
Hawaiian Paradise Park 12 | 2275.6264 | 2819 | x |  |  |  |  | 0
Hawaiian Paradise Park 13 | 5997.9018 | 0 |  | 6156 |  | x |  | 5997.9018
Hawaiian Paradise Park 14 | 1019.0151 | 0 |  | 1200 |  | x |  | 1019.0151
Hawi 11 | 800.8218 | 1302 | x |  |  |  |  | 0
Hawi 12 | 621.6767 | 1594.1762 | x |  |  |  |  | 0
Honokaa 12 | 930.3457 | 624 |  | 1300 |  | x |  | 306.3457
Honokaa 14 | 1245.2312 | 1597 | x |  |  |  |  | 0
Honomu 1 | 364.1415 | 272 |  | 1600 | x |  |  | 92.1415
Host Park 11 | 1580.3826 | 943 |  | 3020 | x |  |  | 637.3826
Host Park 12 | 0 | 0 | x |  |  |  |  | 0
Host Park 13 | 133.1908 | 568 | x |  |  |  |  | 0
Host Park 14 | 837.5728 | 750 |  | 1100 | x |  |  | 87.5728
Huehue 11 | 9208.2903 | 7997 |  | 10200 |  | x |  | 1211.2903
Kahaluu 11 | 3228.8673 | 3221 |  | 4000 |  | x |  | 7.8673
Kahaluu 12 | 1738.1914 | 3138.227 | x |  |  |  |  | 0
Kahaluu 14 | 431.2227 | 1183.068 | x |  |  |  |  | 0
Kahaluu 15 | 2807.7333 | 1857 |  | 5000 | x |  |  | 950.7333
Kailua 11 | 3682.3586 | 6628.674 | x |  |  |  |  | 0
Kailua 12 | 243.9295 | 5558 | x |  |  |  |  | 0
Kailua 15 | 5064.5815 | 8618.3335 | x |  |  |  |  | 0
Kaloko 11 | 2516.5879 | 2756 | x |  |  |  |  | 0
Kaloko 12 | 485.8307 | 215 |  | 759 | x |  |  | 270.8307
Kaloko 13 | 1893.6193 | 1818 |  | 10100 |  | x |  | 75.6193
Kaloko 14 | 70.7179 | 242.651 | x |  |  |  |  | 0
Kamuela 11 | 57.7255 | 1935.845 | x |  |  |  |  | 0
Kamuela 12 | 1866.3065 | 2107 | x |  |  |  |  | 0
Kanoelehua 11 | 1123.6324 | 1223 | x |  |  |  |  | 0
Kanoelehua 1101 | 1209.9828 | 3607 | x |  |  |  |  | 0
Kanoelehua 12 | 965.8793 | 424 |  | 2600 | x |  |  | 541.8793
Kanoelehua 13 | 159.1388 | 81 |  | 1200 | x |  |  | 78.1388
Kanoelehua 14 | 1810.7168 | 2676 | x |  |  |  |  | 0
Kanoelehua 1401 | 1676.2009 | 764 |  | 3000 | x |  |  | 912.2009
Kanoelehua 15 | 2138.0218 | 599 |  | 5000 | x |  |  | 1539.0218
Kanoelehua 17 | 716.242 | 3891.86 | x |  |  |  |  | 0
Kapua 11 | 1652.5649 | 984.7144 |  | 2170 |  | x |  | 667.8505
Kapua 12 | 1106.4303 | 3515.3735 | x |  |  |  |  | 0
Kauhale 11 | 1436.4277 | 864 |  | 2380 |  | x |  | 572.4277
Kauhale 12 | 245.0487 | 0 |  | 2010 |  | x |  | 245.0487
Kaumana 11 | 3608.5316 | 3406 |  | 4600 |  | x |  | 202.5316
Kaumana 12 | 1043.9172 | 1425 | x |  |  |  |  | 0
Kawaihae 11 | 335.205 | 299 |  | 1900 |  | x |  | 36.205
Kawaihae 12 | 587.0548 | 548 |  | 3800 |  | x |  | 39.0548
Kawaihae 13 | 28.4775 | 62 | x |  |  |  |  | 0
Kawailani 11 | 3105.0867 | 2699 |  | 3400 | x |  |  | 406.0867
Kawailani 12 | 2966.9157 | 2912.812 |  | 2967 | x |  |  | 54.1037
Keahole Airport 11 | 1661.9119 | 1252 |  | 1800 |  | x |  | 409.9119
Keahole Airport 12 | 463.2783 | 427.42 |  | 464 |  | x |  | 35.8583
Keahole Airport 13 | 1056.1977 | 940 |  | 2000 |  | x |  | 116.1977
Keahuolu 11 | 321.7469 | 1354 | x |  |  |  |  | 0
Keahuolu 12 | 858.7718 | 2414.4913 | x |  |  |  |  | 0
Kealakehe 11 | 1251.4198 | 1579 | x |  |  |  |  | 0
Kealia 11 | 444.4161 | 898.975 | x |  |  |  |  | 0
Kealia 12 | 745.0361 | 804 | x |  |  |  |  | 0
Keauhou 11 | 1634.3725 | 1674 | x |  |  |  |  | 0
Keauhou 13 | 1818.0874 | 2153.9983 | x |  |  |  |  | 0
Komohana 12 | 4841.5325 | 1355 |  | 6395.0335 |  | x |  | 3486.5325
Komohana 13 | 4401.904 | 6695 | x |  |  |  |  | 0
Komohana 14 | 338.1801 | 851.4 | x |  |  |  |  | 0
Kuakini 11 | 5820.1074 | 4854 |  | 6100 |  | x |  | 966.1074
Kuakini 13 | 1383.9651 | 1019.632 |  | 2038 | x |  |  | 364.3331
Kuakini 14 | 5752.5353 | 4495.5382 |  | 5753 | x |  |  | 1256.9971
Kulani 12 | 47.5741 | 120 | x |  |  |  |  | 0
Kurtistown 12 | 1396.862 | 480 |  | 1800 |  | x |  | 916.862
Lalamilo 11 | 1085.4692 | 1135.9887 | x |  |  |  |  | 0
Lalamilo 12 | 401.4352 | 339.7315 |  | 402 | x |  |  | 61.7037
Laupahoehoe 1 | 132.6548 | 133 | x |  |  |  |  | 0
Laupahoehoe 2 | 280.813 | 190 |  | 281 |  | x |  | 90.813
Maliu Ridge 11 | 511.8608 | 471 |  | 700 | x |  |  | 40.8608
Maliu Ridge 12 | 638.8452 | 816.0253 | x |  |  |  |  | 0
Mauna Lani 11 | 3636.999 | 4848.3655 | x |  |  |  |  | 0
Mauna Lani 13 | 1267.524 | 1701 | x |  |  |  |  | 0
Mauna Lani 14 | 5527.9804 | 2805 |  | 7910 |  | x |  | 2722.9804
Mountain View 11 | 1477.4884 | 2429 | x |  |  |  |  | 0
Mountain View 12 | 364.8617 | 406 | x |  |  |  |  | 0
Namakani Paio | 280.8717 | 128 |  | 1810 |  | x |  | 152.8717
Ookala | 250.8447 | 117 |  | 2440 |  | x |  | 133.8447
Orchid Isle 11 | 90.4411 | 43 |  | 2590 |  | x |  | 47.4411
Orchid Isle 12 | 512.8709 | 219 |  | 2530 |  | x |  | 293.8709
Ouli 11 | 785.0704 | 3381.4935 | x |  |  |  |  | 0
Ouli 12 | 1476.3929 | 4202 | x |  |  |  |  | 0
Paauilo 1 | 365.0963 | 172 |  | 450 |  | x |  | 193.0963
Pahala 11 | 524.153 | 851 | x |  |  |  |  | 0
Pahala 12 | 104.6296 | 310 | x |  |  |  |  | 0
Palani 11 | 142.8112 | 706.6898 | x |  |  |  |  | 0
Palani 12 | 3030.9598 | 4171 | x |  |  |  |  | 0
Palani 13 | 0 | 0 | x |  |  |  |  | 0
Palani 14 | 1033.5648 | 0 |  | 2000 | x |  |  | 1033.5648
Panaewa 11 | 1633.3741 | 2107.258 | x |  |  |  |  | 0
Panaewa 12 | 2992.7861 | 1483 |  | 5465.15 |  | x |  | 1509.7861
Papaaloa 1 | 249.8731 | 401 | x |  |  |  |  | 0
Papaaloa 2 | 163.0838 | 460.2552 | x |  |  |  |  | 0
Poopoomino 11 | 2312.4296 | 2055.3263 |  | 2313 | x |  |  | 257.1033
Poopoomino 12 | 1183.2206 | 4699.7542 | x |  |  |  |  | 0
Poopoomino 13 | 909.4365 | 2117.175 | x |  |  |  |  | 0
Poopoomino 14 | 2211.7952 | 2830 | x |  |  |  |  | 0
Punaluu 11 | 21.4419 | 1118 | x |  |  |  |  | 0
Punaluu 12 | 236.6629 | 678 | x |  |  |  |  | 0
Puueo 11 | 1890.4638 | 836 |  | 2180 |  | x |  | 1054.4638
Puueo 12 | 1942.4687 | 1070 |  | 9080 |  | x |  | 872.4687
Puueo 1402 | 1388.8883 | 4399 | x |  |  |  |  | 0
Puuhuluhulu 11 | 893.3551 | 124 |  | 974 | x |  |  | 769.3551
Puuhuluhulu 12 | 893.3551 | 648 |  | 893.4 | x |  |  | 245.3551
Puukapu 11 | 1861.7836 | 2037 | x |  |  |  |  | 0
Puuwaawaa 11 | 100 | 0 |  | 180 |  |  | x | 100
Puuwaawaa 12 | 362.1279 | 670.1336 | x |  |  |  |  | 0
Royal Hawaiian | 404.0769 | 802 | x |  |  |  |  | 0
Shipman 11 | 507.0666 | 16 |  | 550 | x |  |  | 491.0666
Shipman 12 | 1845.8446 | 1008 |  | 4000 | x |  |  | 837.8446
South Point 11 | 1769.9224 | 1582.338 |  | 2260 | x |  |  | 187.5844
South Point 12 | 70.8419 | 174.042 | x |  |  |  |  | 0
Umauma 11 | 100.6109 | 146 | x |  |  |  |  | 0
Umauma 12 | 173.9471 | 126 |  | 250 | x |  |  | 47.9471
Waika 11 | 149.7195 | 137.0328 |  | 150 | x |  |  | 12.6867
Waika 12 | 2670.9191 | 2445.83 |  | 2671 | x |  |  | 225.0891
Waikii 11 | 566.1992 | 600.6339 | x |  |  |  |  | 0
Waikii 12 | 267.0936 | 0 |  | 3650 |  | x |  | 267.0936
Waikoloa 11 | 2356.2832 | 3314.9605 | x |  |  |  |  | 0
Waikoloa 12 | 5908.8633 | 4055 |  | 5913 |  | x |  | 1853.8633
Waipunahina 11 | 443.5584 | 320.0396 |  | 450 |  | x |  | 123.5189
Wright Road 11 | 1262.6678 | 1606 | x |  |  |  |  | 0

## Maui Island HC Results
Return to Assumptions Summary
Maui Island Hosting Capacity Analysis Results by Circuit - High Forecast
The Hosting Capacity Analysis Results by Circuit shows the Existing Hosting Capacity (HC) rating compared to the Total 2025 DER Forecast. The Total 2025 DER is the total anticipated DER in year 2025. Circuits with existing hosting capacity able to accommodate the Total 2025 DER are marked with an “X” in the Existing HC Satisfies Need column. Circuits with updated hosting capacity able to accommodate the Total 2025 DER without any modifications are marked with an “X” in the Updated HC (w/o Mods) Satisfies Need column. Circuits with updated hosting capacity and modifications (non-infrastructure investment solutions) able to accommodate the Total 2025 DER are marked with an “X” in the Updated HC (w/ Mods) Satisfies Needs column. Circuits that require infrastructure investment solutions are marked with an "X" in the Solution Option Required column. Additional details for these circuits are shown in the Grid Needs Assessment (GNA) tables. The Circuit Count provides a summary of the hosting caapcity results. The Hosting Capacity Increase (kW) is an estimate of the increase in hosting capacity due to the total updated hosting capacity available for all circuits as a result of this analysis. The Total 2025 DER forecast and hosting capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
Circuit Name | Total 2025 DER (kW) | Existing HC (kW) | Existing HC Satisfies Need | Updated HC (kW) | Updated HC (w/o Mods) Satisfies Need | Updated HC (w/ Mods) Satisfies Need | Solution Option Required | HC Increase (kW) | Circuit Count | Total
Haiku 16/1358 | 3088.7195 | 3377.73 | x |  |  |  |  | 0 | Total Circuits | 88
Haiku 16/1361 | 996.625 | 1261.01 | x |  |  |  |  | 0 | Existing HC Satisfies Need | 52
Hana 41/10277 | 108.2175 | 0 |  | 181 | x |  |  | 108.2175 | Updated HC (w/o Modifications) | 16
Hana 41/537 | 174.2343 | 0 |  | 229 | x |  |  | 174.2343 | Updated HC (w Modifications) | 13
Hana 41/6528 | 54.5614 | 0 |  | 116 | x |  |  | 54.5614 | Solution Option Required | 7
Huelo 74A/Huelo | 224.3682 | 192 |  | 370 |  |  | x | 32.3682
Kahului 8/1264 | 1229.3259 | 3265.9 | x |  |  |  |  | 0
Kahului 8/1265 | 3574.7485 | 3684.7 | x |  |  |  |  | 0
Kahului 8/4048 | 1600.3185 | 1420 |  | 2390 |  | x |  | 180.3185 | Hosting Capacity Increase (kW) | 64213.4278
Kahului 8/4049 | 1360.0921 | 338 |  | 2200 |  | x |  | 1022.0921
Kahului 8/4050 | 589.8388 | 955.2 | x |  |  |  |  | 0
Kailua 9/Kailua | 18.7796 | 67.082 | x |  |  |  |  | 0
Kanaha 2/1244 | 2225.1818 | 5049.425 | x |  |  |  |  | 0
Kanaha 2/1245 | 1506.338 | 1861.619 | x |  |  |  |  | 0
Kanaha 2/1304 | 2431.4838 | 4447.5145 | x |  |  |  |  | 0
Kanaha 2/1305 | 2953.4238 | 3973.427 | x |  |  |  |  | 0
Kanaha 2/1347 | 2936.9866 | 6172.32 | x |  |  |  |  | 0
Kanaha 2/1348 | 1042.6891 | 8361.8 | x |  |  |  |  | 0
Kaonoulu/1590 | 5522.9132 | 0 |  | 6000 | x |  |  | 5522.9132
Kaonoulu/1591 | 1494.2549 | 0 |  | 3000 | x |  |  | 1494.2549
Kauhikoa 98/1295 | 1169.6195 | 1142.91 |  | 1200 |  | x |  | 26.7095
Keanae 42/Keanae | 40.9334 | 173.315 | x |  |  |  |  | 0
Kihei 35/1253 | 2167.1787 | 5087.26 | x |  |  |  |  | 0
Kihei 35/1254 | 4761.2795 | 6100.11 | x |  |  |  |  | 0
Kihei 35/1384 | 9889.9494 | 1158.9 |  | 9900 | x |  |  | 8731.0494
Kihei 35/1385 | 1807.2199 | 1847.3 | x |  |  |  |  | 0
Kihei 35/1473 | 4452.0817 | 0 |  | 5656.5 | x |  |  | 4452.0817
Kihei 35/1515 | 9094.1708 | 7610.25 |  | 9300 |  |  | x | 1483.9208
Kuau 73/4066 | 1027.9114 | 551.5 |  | 1940 |  | x |  | 476.4114
Kuihelani 209/1653 | 6119.143 | 0 |  | 7019.36 |  | x |  | 6119.143
Kuihelani 209/1708 | 3411.1819 | 0 |  | 4260 |  | x |  | 3411.1819
Kula 13/1237 | 3903.8399 | 2658.6 |  | 4500 |  |  | x | 1245.2399
Kula 13/1238 | 3963.9681 | 3227 |  | 5500 |  | x |  | 736.9681
Kula Ag Park 55/1322 | 925.4274 | 448.53 |  | 1252 | x |  |  | 476.8974
Lahaina 34/1221 | 2883.2041 | 4090 | x |  |  |  |  | 0
Lahaina 34/1223 | 6876.5913 | 3078.11 |  | 6876.6 | x |  |  | 3798.4813
Lahaina 34/1225 | 807.6563 | 2139.26 | x |  |  |  |  | 0
Lahaina 34/1226 | 452.0446 | 1485 | x |  |  |  |  | 0
Lahaina 34/1390 | 3615.4947 | 0 |  | 4000 | x |  |  | 3615.4947
Lahaina 34/1397 | 282.3201 | 1797.4 | x |  |  |  |  | 0
Lahaina 34/1398 | 5882.4004 | 971.6 |  | 7000 |  |  | x | 4910.8004
Maalaea 39/1285 | 1150.6069 | 4212.3 | x |  |  |  |  | 0
Maalaea 39/1286 | 1551.3174 | 2420.01 | x |  |  |  |  | 0
Mahinahina 50/1219 | 3167.461 | 12477.51 | x |  |  |  |  | 0
Mahinahina 50/1380 | 940.156 | 1283.48 | x |  |  |  |  | 0
Mahinahina 50/1381 | 4302.7238 | 5289 | x |  |  |  |  | 0
Makawao 12/1234 | 1153.8805 | 1385.4 | x |  |  |  |  | 0
Makawao 12/1235 | 1896.4738 | 1536.8 |  | 2474.1925 | x |  |  | 359.6738
Makawao 12/1236 | 1556.3929 | 1315.9 |  | 2500 |  | x |  | 240.4929
Maui Hardwoods 75/522 | 529.2093 | 1503.7 | x |  |  |  |  | 0
Napili 29/1232 | 707.1152 | 4997.55 | x |  |  |  |  | 0
Napili 29/1420 | 3527.1772 | 2453.72 |  | 4252 | x |  |  | 1073.4572
Napili 29/1421 | 1330.2438 | 1592.6 | x |  |  |  |  | 0
Onehee 40/4055 | 1754.7855 | 1700 |  | 2000 |  |  | x | 54.7855
Onehee 40/4056 | 719.6833 | 743.38 | x |  |  |  |  | 0
Paia Mauka 93/4042 | 1738.348 | 521.5 |  | 2000 |  |  | x | 1216.848
Peahi 94/1294 | 2043.9477 | 1456.7 |  | 2430 |  | x |  | 587.2477
Pukalani 17/1282 | 4185.6686 | 2927.3 |  | 5983.29 |  | x |  | 1258.3686
Pukalani 17/1283 | 9.2828 | 1060.14 | x |  |  |  |  | 0
Pukalani 17/1308 | 5846.8447 | 5155.9 |  | 9000 | x |  |  | 690.9447
Pukalani 17/1309 | 620.4524 | 1314.71 | x |  |  |  |  | 0
Puukolii 23/1270 | 7583.3544 | 14132.5 | x |  |  |  |  | 0
Puukolii 23/1271 | 1573.6056 | 4445.9 | x |  |  |  |  | 0
Puukolii 23/1272 | 4249.326 | 5865.4 | x |  |  |  |  | 0
Puukolii 23/1273 | 146.2738 | 730.72 | x |  |  |  |  | 0
Spreckelsville 92/4043 | 1434.0762 | 0 |  | 1450 |  | x |  | 1434.0762
Waiehu 43/1378 | 2974.3343 | 3261.42 | x |  |  |  |  | 0
Waiehu 43/1379 | 4992.5604 | 3922.55 |  | 5000 | x |  |  | 1070.0104
Waiinu 36/1266 | 1496.3062 | 3822.12 | x |  |  |  |  | 0
Waiinu 36/1267 | 802.949 | 1759.85 | x |  |  |  |  | 0
Waiinu 36/1492 | 1362.2565 | 3484.74 | x |  |  |  |  | 0
Waiinu 36/1493 | 11150.6617 | 8021.54 |  | 12000 |  | x |  | 3129.1217
Waiinu 36/2030 | 428.9148 | 848.9 | x |  |  |  |  | 0
Waikapu 77/524 | 0 | 826.914 | x |  |  |  |  | 0
Wailea 25/1280 | 3810.5276 | 4155.22 | x |  |  |  |  | 0
Wailea 25/1281 | 938.1427 | 3060.13 | x |  |  |  |  | 0
Wailea 25/1320 | 3325.4944 | 6017.472 | x |  |  |  |  | 0
Wailea 25/1321 | 42.6286 | 3997.46 | x |  |  |  |  | 0
Wailea 25/1395 | 653.7488 | 4018.53 | x |  |  |  |  | 0
Wailea 25/1396 | 1206.7689 | 3574.2 | x |  |  |  |  | 0
Wailea 25/1517 | 3718.7016 | 2705.41 |  | 4389.382 |  |  | x | 1013.2916
Wailea 25/1518 | 2251.2429 | 1632.631 |  | 4000 |  | x |  | 618.6119
Wailuku 3/1290 | 6004.2268 | 3242.2 |  | 6004.23 | x |  |  | 2762.0268
Wailuku 3/1447 | 4045.8822 | 5574.3 | x |  |  |  |  | 0
Wailuku 3/4031 | 769.8748 | 1079.01 | x |  |  |  |  | 0
Wailuku 3/4037 | 1204.3412 | 573.21 |  | 1300 | x |  |  | 631.1312
Wailuku Heights 18/493 | 1182.9496 | 1300 | x |  |  |  |  | 0
Wailuku Heights 18/529 | 769.3987 | 1400 | x |  |  |  |  | 0

## Lanai HC Results
Return to Assumptions Summary
Lana‘i Hosting Capacity Analysis Results by Circuit - High Forecast
The Hosting Capacity Analysis Results by Circuit shows the Existing Hosting Capacity (HC) rating compared to the Total 2025 DER Forecast. The Total 2025 DER is the total anticipated DER in year 2025. Circuits with existing hosting capacity able to accommodate the Total 2025 DER are marked with an “X” in the Existing HC Satisfies Need column. Circuits with updated hosting capacity able to accommodate the Total 2025 DER without any modifications are marked with an “X” in the Updated HC (w/o Mods) Satisfies Need column. Circuits with updated hosting capacity and modifications (non-infrastructure investment solutions) able to accommodate the Total 2025 DER are marked with an “X” in the Updated HC (w/ Mods) Satisfies Needs column. Circuits that require infrastructure investment solutions are marked with an "X" in the Solution Option Required column. Additional details for these circuits are shown in the Grid Needs Assessment (GNA) tables. The Circuit Count provides a summary of the hosting caapcity results. The Hosting Capacity Increase (kW) is an estimate of the increase in hosting capacity due to the total updated hosting capacity available for all circuits as a result of this analysis. The Total 2025 DER forecast and hosting capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
Circuit Name | Total 2025 DER (kW) | Existing HC (kW) | Existing HC Satisfies Need | Updated HC (kW) | Updated HC (w/o Mods) Satisfies Need | Updated HC (w/ Mods) Satisfies Need | Solution Option Required | HC Increase (kW) | Circuit Count | Total
Miki Basin PP 302/1208 | 505.8074 | 386 |  | 2700 |  |  | x | 119.8074 | Total Circuits | 3
Miki Basin PP 302/1210 | 2204.1139 | 2154 |  | 3900 |  |  | x | 50.1139 | Existing HC Satisfies Need | 1
Miki Basin PP 302/1212 | 584.7177 | 2664.3 | x |  |  |  |  | 0 | Updated HC (w/o Modifications) | 0
[9 empty] | Updated HC (w Modifications) | 0
[9 empty] | Solution Option Required | 2
[9 empty] | Hosting Capacity Increase (kW) | 169.9213

## Molokai HC Results
Return to Assumptions Summary
Moloka‘i Hosting Capacity Analysis Results by Circuit - High Forecast
The Hosting Capacity Analysis Results by Circuit shows the Existing Hosting Capacity (HC) rating compared to the Total 2025 DER Forecast. The Total 2025 DER is the total anticipated DER in year 2025. Circuits with existing hosting capacity able to accommodate the Total 2025 DER are marked with an “X” in the Existing HC Satisfies Need column. Circuits with updated hosting capacity able to accommodate the Total 2025 DER without any modifications are marked with an “X” in the Updated HC (w/o Mods) Satisfies Need column. Circuits with updated hosting capacity and modifications (non-infrastructure investment solutions) able to accommodate the Total 2025 DER are marked with an “X” in the Updated HC (w/ Mods) Satisfies Needs column. Circuits that require infrastructure investment solutions are marked with an "X" in the Solution Option Required column. Additional details for these circuits are shown in the Grid Needs Assessment (GNA) tables. The Circuit Count provides a summary of the hosting caapcity results. The Hosting Capacity Increase (kW) is an estimate of the increase in hosting capacity due to the total updated hosting capacity available for all circuits as a result of this analysis. The Total 2025 DER forecast and hosting capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
Circuit Name | Total 2025 DER (kW) | Existing HC (kW) | Existing HC Satisfies Need | Updated HC (kW) | Updated HC (w/o Mods) Satisfies Need | Updated HC (w/ Mods) Satisfies Need | Solution Option Required | HC Increase (kW) | Circuit Count | Total
Palaau PP 81/105A | 1332.6152 | 1025.5 |  | 1350 |  |  | x | 307.1152 | Total Circuits | 8
Palaau PP 81/106B | 353.9487 | 282.2 |  | 550 |  |  | x | 71.7487 | Existing HC Satisfies Need | 3
Palaau PP 81/109B | 180.8604 | 125 |  | 800 |  |  | x | 55.8604 | Updated HC (w/o Modifications) | 0
Palaau PP 81/110B | 356.6768 | 212 |  | 1000 |  |  | x | 144.6768 | Updated HC (w Modifications) | 0
Palaau PP 81/111A | 1669.6207 | 823 |  | 2000 |  |  | x | 846.6207 | Solution Option Required | 5
Puunana 80/1466 | 54.861 | 1061 | x |  |  |  |  | 0
Puunana 80/1467 | 267.7874 | 613 | x |  |  |  |  | 0
Puunana 80/1468 | 15.5768 | 532 | x |  |  |  |  | 0
[9 empty] | Hosting Capacity Increase (kW) | 1426.0218

## Oahu Total DER
Return to Assumptions Summary
O‘ahu Total Anticipated DER and Hosting Capacity by Circuit (kW) - High Forecast
The Total Anticipated DER is the sum of the Executed DER and the Adjusted DER Growth by Circuit. The Executed DER for each circuit is the aggregated program size (kW) of all executed DER programs on that circuit as of December 31, 2020. The Hosting Capacity (HC) by circuit is provided for comparison. The Existing HC is the current hosting capacity for each circuit. The Updated HC is the updated hosting capacity as a result of this analysis. The Executed DER, Total Anticipated DER, and Hosting Capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
|  | Total Anticipated DER |  |  |  |  | Hosting Capacity
Circuit | Executed DER | 2021 | 2022 | 2023 | 2024 | 2025 | Existing HC | Updated HC
AHUA | 959.7 | 1195.224 | 1513.886 | 1628.904 | 1870.962 | 1972.899 | 1561 | 6080
AIEA | 2895.347 | 3188.942 | 3623.002 | 3866.158 | 4165.416 | 4563.117 | 3601 | 5700
AINA KOA | 1887.727 | 2480.454 | 3189.81 | 3783.519 | 4037.214 | 4628.381 | 2951 | 4926
ANOI | 3761.365 | 4043.401 | 4301.908 | 4548.644 | 4707.782 | 4854.073 | 3794 | 6360
ANUU | 3028.055 | 3353.33 | 3816.036 | 4271.982 | 4708.813 | 4993.407 | 4073 | 5321.2
BEACH LOTS | 3079.172 | 3513.563 | 3937.852 | 4384.442 | 4732.37 | 4979.795 | 4712 | 6500
CKT 16 | 2214.53 | 6289.125 | 7289.125 | 7589.125 | 7890.523 | 7991.921 | 6611 | 10012
DIAMOND HEAD | 290.68 | 646.859 | 1630.537 | 2155.05 | 2214.817 | 2709.38 | 1452 | 3280
EKEKELA | 770.425 | 822.754 | 923.395 | 988.357 | 1037.999 | 1096.058 | 1070 | 1312
EWA BEACH 3 | 2618.331 | 2973.889 | 3811.989 | 4422.514 | 4769.663 | 4998.736 | 4029 | 4999
EWA BEACH 4 | 4230.719 | 4803.015 | 5841.846 | 6869.572 | 7540.99 | 8045.949 | 5966 | 8046
EWA NUI 2 | 3539.612 | 4191.669 | 5706.669 | 7051.217 | 7564.637 | 8088.111 | 6024 | 8089
FARMERS RD | 947.106 | 1121.22 | 1251.243 | 1521.192 | 1574.415 | 1746.258 | 1411 | 1746.26
FORT WEAVER 2 | 3885.913 | 4659.843 | 5416.524 | 6116.085 | 6610.341 | 7051.215 | 6321 | 7052
FORT WEAVER 3 | 3681.494 | 4151.791 | 5053.636 | 5536.699 | 6107.843 | 6589.204 | 5950 | 6590
HAHAIONE | 2044.82 | 2181.77 | 2753.645 | 3027.433 | 3290.594 | 3453.905 | 3366 | 3964.8
HAUULA | 1534.12 | 6542.92 | 6760.357 | 6924.719 | 7036.517 | 7142.088 | 2802 | 8630
HEIGHTS | 1026.56 | 1090.324 | 1184.394 | 1266.222 | 1324.124 | 1397.452 | 1145 | 1397.5
HIKINA | 135.11 | 144.498 | 212.676 | 224.082 | 240.392 | 253.924 | 220 | 491.8
HILA 4 | 400 | 400 | 400 | 400 | 400 | 400 | 0 | 2323
HOAEAE 1 | 2848.915 | 3517.746 | 4560.658 | 5323.716 | 5898.774 | 6504.755 | 5113 | 8445
HOAEAE 3 | 1134.32 | 2089.945 | 2508.046 | 2899.454 | 3650.499 | 4037.225 | 2488 | 4038
KAENA PT | 1568.97 | 1898.118 | 2479.183 | 2830.336 | 3075.562 | 3328.799 | 2739 | 3328.8
KAHALA | 1333.742 | 1621.622 | 2069.228 | 2212.343 | 2518.643 | 2591.055 | 1976 | 2591.06
KAHALA 3 | 1013.192 | 5232.391 | 5784.739 | 6401.451 | 6785.174 | 7171.717 | 1609 | 7269
KAHALOA | 1033.26 | 1113.238 | 1249.227 | 1377.716 | 1445.387 | 1502.763 | 1407 | 1630
KAHUKU | 1453.58 | 1943.442 | 2580.405 | 2850.223 | 3150.78 | 3363.156 | 2422 | 4240
KAI-HARDING | 347.43 | 361.223 | 383.613 | 428.468 | 458.639 | 482.05 | 471 | 483
KAILUA 1 | 2023.488 | 2576.295 | 2997.425 | 3492.561 | 3613.212 | 4008.813 | 3746 | 5341.3
KAILUA HTS | 3745.181 | 4105.782 | 4846.993 | 5346.871 | 5693.321 | 5946.756 | 5755 | 6120
KAINALU | 1452.85 | 1765.175 | 2206.391 | 2393.34 | 2522.262 | 2598.058 | 1047 | 2625.3
KALAHEO | 973.041 | 1063.267 | 1137.569 | 1236.751 | 1365.894 | 1637.376 | 1462 | 1800
KALIHI ST | 676.04 | 708.047 | 841.934 | 973.679 | 1025.305 | 1097.737 | 1021 | 1620
KALOI 1 | 714.56 | 814.56 | 814.56 | 1114.56 | 1114.56 | 1314.56 | 612 | 2979
KAM TERRACE | 824.24 | 954.179 | 1230.489 | 1345.728 | 1745.77 | 1934.804 | 1323 | 3800
KAPOLEI 4 | 1288.9 | 6442.099 | 6640.903 | 6782.757 | 6869.61 | 6970.09 | 2966 | 6971
KAWAILOA | 1109.9 | 1224.164 | 1613.753 | 1736.507 | 1821.619 | 1920.292 | 1133 | 2467.5
KEWALO | 2008.74 | 2246.264 | 2574.019 | 2840.094 | 7689.339 | 7888.251 | 7024 | 11692
KILAUEA 4KV | 869.41 | 942.877 | 1027.67 | 1091.279 | 1152.948 | 1231.076 | 962 | 1330
KOLOA | 654.41 | 814.528 | 1002.328 | 1269.133 | 1444.334 | 1594.945 | 1281 | 1594.95
KUAPA 2 | 984.92 | 1320.244 | 1642.825 | 2003.643 | 2261.647 | 2364.274 | 1891 | 6740
KUILIMA 1 | 776.588 | 898.003 | 1083.444 | 1344.684 | 1486.937 | 1605.071 | 1524 | 1605.08
LOWREY | 869.843 | 941.839 | 1044.921 | 1162.695 | 1278.414 | 1359.511 | 1129 | 1380
MACHADO ST | 543.26 | 588.938 | 680.549 | 749.847 | 800.87 | 854.629 | 736 | 1500
MAKAHA VALLEY | 842.075 | 1016.95 | 1407.392 | 1607.724 | 1670.514 | 1829.603 | 1725 | 1830
MAKAKILO 1 | 2270.155 | 2704.458 | 3211.85 | 3702.721 | 4016.698 | 4336.67 | 3988 | 4539
MAKAKILO 2 | 4656.717 | 5352.743 | 8956.269 | 9674.667 | 10107.494 | 10569.553 | 8472 | 10570
MANOA 2 | 724.1 | 803.385 | 956.723 | 1045.804 | 1154.25 | 1228.589 | 1089 | 2180
MANOA-PIIKOI | 963.705 | 1110.743 | 1321.487 | 1521.213 | 1743.939 | 1963.032 | 1553 | 2090
MAPUNAPUNA | 228.27 | 453.308 | 777.78 | 877.78 | 1077.78 | 1077.78 | 371 | 3835
MAUKA | 6030.66 | 6846.429 | 8060.027 | 8827.549 | 9370.865 | 10282.251 | 8350 | 10283
MAUNALANI | 1424.645 | 1507.27 | 1763.082 | 1914.519 | 2034.077 | 2121.762 | 2057 | 2159
MIKILUA 3 | 3777.53 | 4030.411 | 4467.021 | 4944.162 | 5151.177 | 5439.32 | 4761 | 5440
MIKILUA 4 | 5016.675 | 5439.649 | 6191.689 | 6982.478 | 7465.256 | 7652.835 | 3514 | 7653
MIKILUA 5 | 5507.509 | 6018.007 | 6778.973 | 7438.552 | 7995.403 | 8544.115 | 7382 | 8545
NUUANU | 337.63 | 505.586 | 599.216 | 783.504 | 926.704 | 978.188 | 719 | 2160
OCEAN POINTE 1 | 3810.537 | 4135.399 | 4924.928 | 5323.343 | 5741.858 | 6063.05 | 5876 | 6064
OCEAN POINTE 2 | 3411.585 | 3834.458 | 4380.659 | 4788.921 | 5143.238 | 5453.231 | 5280 | 5454
OCEAN POINTE 4 | 1094.63 | 1206.762 | 1360.828 | 1497.841 | 1600.983 | 1712.819 | 1362 | 1713
ONEAWA | 804.874 | 877.482 | 956.677 | 1065.403 | 1130.101 | 1178.436 | 908 | 2160
PAHIA | 1073.18 | 1479.566 | 1745.616 | 1946.144 | 2063.986 | 2309.315 | 1505 | 4310
PAUOA 2 | 2832.128 | 3436.604 | 4215.545 | 4676.042 | 5056.07 | 5391.719 | 4522 | 7130
PIIKOI 8 | 1457.95 | 1680.567 | 2048.373 | 2309.757 | 2582.721 | 2719.564 | 1993 | 3469
PORTLOCK | 905.825 | 1362.024 | 2925.664 | 3534.793 | 4449.448 | 5120.007 | 4113 | 5580
PUNCHBOWL | 425.214 | 532.936 | 682.771 | 777.984 | 834.459 | 883.877 | 656 | 1240
QUEENS 2 | 1232.308 | 1423.007 | 1520.598 | 1601.045 | 1678.897 | 1732.816 | 1722 | 1732.82
WAHIAWA HTS | 2684.243 | 2965.482 | 3498.719 | 3852.82 | 4178.302 | 4428.387 | 4206 | 4428.39
WAIALUA | 1335.065 | 1476.942 | 1785.708 | 2232.172 | 2393.989 | 2641.675 | 1711 | 3301.7
WAIHEE 2 | 1278.555 | 1522.633 | 1833.442 | 2111.419 | 2266.139 | 2419.175 | 2101 | 2419.18
WAIHEE 3 | 395.21 | 450.417 | 686.846 | 754.108 | 843.698 | 887.709 | 660 | 887.71
WAIHEE 4 | 2455.351 | 2861.66 | 3313.07 | 3723.28 | 3998.975 | 4279.849 | 4189 | 4279.85
WAILUPE | 4300.349 | 5053.974 | 6261.821 | 7397.683 | 7842.446 | 8165.261 | 6579 | 8653
WAIMALU 3 | 4143.16 | 4587.794 | 5228.303 | 5730.71 | 6086.705 | 6430.662 | 5984 | 6430.664
WAIMANALO | 900.716 | 1172.918 | 1727.273 | 1914.353 | 2069.179 | 2320.401 | 2248 | 2480
WAIMANO 5 | 1329.634 | 1456.215 | 1701.186 | 1884.327 | 2032.473 | 2180.37 | 2078 | 2180.37
WAIMANO HOME RD | 3078.37 | 3516.863 | 4317.704 | 4789.261 | 5200.059 | 5554.959 | 5099 | 5554.96
WAIMEA 2 | 1872.168 | 2032.663 | 2621.496 | 2983.414 | 3170.614 | 3396.283 | 3168 | 3495
WAIPAHU | 4373.156 | 5430.007 | 7075.653 | 8356.098 | 9357.571 | 10233.366 | 8874 | 10233.4
WAI-WILHELMINA | 1034.205 | 1097.676 | 1204.157 | 1314.539 | 1368.484 | 1456.392 | 1376 | 1480
WILIWILI 1 | 1692.935 | 1829.379 | 2042.57 | 2198.531 | 2296.944 | 2426.617 | 2293 | 4090
WILIWILI 2 | 1947.807 | 2085.053 | 2241.57 | 2365.497 | 2445.675 | 2563.058 | 2126 | 2566

## Hawaii Island Total DER
Return to Assumptions Summary
Hawai‘i Island Total Anticipated DER and Hosting Capacity by Circuit (kW) - High Forecast
The Total Anticipated DER is the sum of the Executed DER and the Adjusted DER Growth by Circuit. The Executed DER for each circuit is the aggregated program size (kW) of all executed DER programs on that circuit as of December 31, 2020. The Hosting Capacity (HC) by circuit is provided for comparison. The Existing HC is the current hosting capacity for each circuit. The Updated HC is the updated hosting capacity as a result of this analysis. The Executed DER, Total Anticipated DER, and Hosting Capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
|  | Total Anticipated DER |  |  |  |  | Hosting Capacity
Circuit | Executed DER | 2021 | 2022 | 2023 | 2024 | 2025 | Existing HC | Updated HC
Captain Cook 12 | 1118.431 | 1266.4162 | 1428.5274 | 1578.1445 | 1724.4912 | 1873.5347 | 1795 | 7000
Halaula 1 | 585.276 | 662.7168 | 747.5497 | 825.8445 | 902.4279 | 980.4225 | 743 | 1375
Hale Pohaku 11 | 232.55 | 263.3199 | 297.0269 | 328.136 | 358.5652 | 389.5551 | 85 | 3730
Hale Pohaku 12 | 98.1 | 111.0801 | 125.2992 | 138.4225 | 151.2588 | 164.3318 | 83 | 2370
Hawaiian Paradise Park 13 | 3580.5257 | 4054.283 | 4573.263 | 5052.2447 | 5520.7564 | 5997.9018 | 0 | 6156
Hawaiian Paradise Park 14 | 608.3143 | 688.8035 | 776.9757 | 858.3524 | 937.9503 | 1019.0151 | 0 | 1200
Honokaa 12 | 555.382 | 628.8674 | 709.3673 | 783.6631 | 856.3348 | 930.3457 | 624 | 1300
Honomu 1 | 217.379 | 246.1415 | 277.6495 | 306.7292 | 335.1733 | 364.1415 | 272 | 900
Host Park 11 | 943.43 | 1068.26 | 1205.0056 | 1331.2121 | 1454.6599 | 1580.3826 | 943 | 3020
Host Park 14 | 500 | 566.1575 | 638.6301 | 705.5172 | 770.9421 | 837.5728 | 750 | 1100
Huehue 11 | 5497.009 | 6224.3458 | 7021.1108 | 7756.4684 | 8475.7518 | 9208.2903 | 7997 | 10200
Kahaluu 11 | 1987.97 | 2231.161 | 2497.5659 | 2743.4388 | 2983.9371 | 3228.8673 | 3221 | 4000
Kahaluu 15 | 1676.113 | 1897.8879 | 2140.8324 | 2365.053 | 2584.3723 | 2807.7333 | 1857 | 5000
Kaloko 12 | 290.023 | 328.3974 | 370.4348 | 409.2324 | 447.1819 | 485.8307 | 215 | 759
Kaloko 13 | 1231.18 | 1361.0048 | 1503.2222 | 1634.4787 | 1762.866 | 1893.6193 | 1818 | 10100
Kanoelehua 12 | 584.655 | 659.3673 | 741.2114 | 816.7476 | 890.6327 | 965.8793 | 424 | 2600
Kanoelehua 13 | 95 | 107.5699 | 121.3397 | 134.0483 | 146.479 | 159.1388 | 81 | 1200
Kanoelehua 1401 | 1000.63 | 1133.0284 | 1278.0649 | 1411.9233 | 1542.8557 | 1676.2009 | 764 | 3000
Kanoelehua 15 | 1276.32 | 1445.1963 | 1630.1927 | 1800.9313 | 1967.9378 | 2138.0218 | 599 | 5000
Kapua 11 | 1486.286 | 1518.8733 | 1554.5713 | 1587.518 | 1619.7445 | 1652.5649 | 984.7144 | 2170
Kauhale 11 | 865.555 | 977.4346 | 1099.9938 | 1213.1071 | 1323.748 | 1436.4277 | 864 | 2380
Kauhale 12 | 146.285 | 165.6407 | 186.844 | 206.4132 | 225.5545 | 245.0487 | 0 | 2010
Kaumana 11 | 2154.16 | 2439.1877 | 2751.4228 | 3039.5937 | 3321.4655 | 3608.5316 | 3406 | 4600
Kawaihae 11 | 200.105 | 226.5819 | 255.5862 | 282.355 | 308.5388 | 335.205 | 299 | 1900
Kawaihae 12 | 350.45 | 396.8198 | 447.6158 | 494.497 | 540.3534 | 587.0548 | 548 | 3800
Kawailani 11 | 1853.622 | 2098.884 | 2367.5576 | 2615.5243 | 2858.0707 | 3105.0867 | 2699 | 3400
Kawailani 12 | 1771.139 | 2005.4873 | 2262.2054 | 2499.1379 | 2730.8914 | 2966.9157 | 2912.812 | 2967
Keahole Airport 11 | 992.1 | 1123.3697 | 1267.1698 | 1399.8872 | 1529.7034 | 1661.9119 | 1252 | 1800
Keahole Airport 12 | 276.56 | 313.153 | 353.2391 | 390.2357 | 426.4235 | 463.2783 | 427.42 | 464
Keahole Airport 13 | 630.511 | 713.9371 | 805.3266 | 889.6727 | 972.175 | 1056.1977 | 940 | 2000
Komohana 12 | 2890.216 | 3272.635 | 3691.5579 | 4078.194 | 4456.3787 | 4841.5325 | 1355 | 6395.0335
Kuakini 11 | 3474.389 | 3934.1028 | 4437.6988 | 4902.4822 | 5357.1058 | 5820.1074 | 4854 | 6100
Kuakini 13 | 826.176 | 935.4915 | 1055.2417 | 1165.7627 | 1273.8678 | 1383.9651 | 1019.632 | 2038
Kuakini 14 | 3434.051 | 3888.4275 | 4386.1767 | 4845.5639 | 5294.9093 | 5752.5353 | 4495.5382 | 5753
Kurtistown 12 | 833.875 | 944.2092 | 1065.0754 | 1176.6263 | 1285.7388 | 1396.862 | 480 | 1800
Lalamilo 12 | 239.642 | 271.3502 | 306.0852 | 338.1431 | 369.5002 | 401.4352 | 339.7315 | 402
Laupahoehoe 2 | 167.635 | 189.8156 | 214.1135 | 236.5387 | 258.4738 | 280.813 | 190 | 281
Maliu Ridge 11 | 305.562 | 345.9924 | 390.2822 | 431.1585 | 471.1412 | 511.8608 | 471 | 700
Mauna Lani 14 | 3300 | 3736.6395 | 4214.9587 | 4656.4133 | 5088.2182 | 5527.9804 | 2805 | 7910
Namakani Paio | 167.67 | 189.8553 | 214.1582 | 236.5881 | 258.5277 | 280.8717 | 128 | 1810
Ookala | 149.745 | 169.5585 | 191.2633 | 211.2953 | 230.8895 | 250.8447 | 117 | 2440
Orchid Isle 11 | 53.99 | 61.1337 | 68.9593 | 76.1817 | 83.2463 | 90.4411 | 43 | 2590
Orchid Isle 12 | 306.165 | 346.6752 | 391.0524 | 432.0093 | 472.071 | 512.8709 | 219 | 2530
Paauilo 1 | 217.949 | 246.7869 | 278.3776 | 307.5335 | 336.0521 | 365.0963 | 172 | 450
Palani 14 | 617 | 698.6384 | 788.0695 | 870.6082 | 951.3426 | 1033.5648 | 0 | 3970
Panaewa 12 | 1824.71 | 2053.6295 | 2304.4007 | 2535.8446 | 2762.2294 | 2992.7861 | 1483 | 5465.15
Poopoomino 11 | 1380.435 | 1563.0873 | 1763.1747 | 1947.8412 | 2128.471 | 2312.4296 | 2055.3263 | 2313
Puueo 11 | 1128.537 | 1277.8594 | 1441.4354 | 1592.4045 | 1740.0735 | 1890.4638 | 836 | 2180
Puueo 12 | 1159.582 | 1313.0121 | 1481.0879 | 1636.21 | 1787.9413 | 1942.4687 | 1070 | 9080
Puuhuluhulu 11 | 533.3 | 603.8636 | 681.1629 | 752.5046 | 822.2869 | 893.3551 | 124 | 974
Puuhuluhulu 12 | 533.3 | 603.8636 | 681.1629 | 752.5046 | 822.2869 | 893.3551 | 648 | 893.4
Puuwaawaa 11 | 0 | 100 | 100 | 100 | 100 | 100 | 0 | 180
Shipman 11 | 302.7 | 342.7518 | 386.6267 | 427.1201 | 466.7284 | 507.0666 | 16 | 550
Shipman 12 | 1101.901 | 1247.699 | 1407.4143 | 1554.8201 | 1699.0038 | 1845.8446 | 1008 | 4000
South Point 11 | 608.856 | 1439.4168 | 1527.6675 | 1609.1167 | 1688.7855 | 1769.9224 | 1582.338 | 2260
Umauma 12 | 103.84 | 117.5796 | 132.6307 | 146.5218 | 160.1093 | 173.9471 | 126 | 250
Waika 11 | 89.377 | 101.2029 | 114.1577 | 126.114 | 137.809 | 149.7195 | 137.0328 | 150
Waika 12 | 1594.44 | 1805.4084 | 2036.5148 | 2249.8096 | 2458.442 | 2670.9191 | 2445.83 | 2671
Waikii 12 | 159.445 | 180.542 | 203.6528 | 224.9824 | 245.8457 | 267.0936 | 0 | 3650
Waikoloa 12 | 3527.373 | 3994.0974 | 4505.3732 | 4977.2444 | 5438.801 | 5908.8633 | 4055 | 5913
Waipunahina 11 | 264.788 | 299.8234 | 338.2032 | 373.625 | 408.2725 | 443.5584 | 320.0396 | 450

## Maui Total DER
Return to Assumptions Summary
Maui Island Total Anticipated DER and Hosting Capacity by Circuit (kW) - High Forecast
The Total Anticipated DER is the sum of the Executed DER and the Adjusted DER Growth by Circuit. The Executed DER for each circuit is the aggregated program size (kW) of all executed DER programs on that circuit as of December 31, 2020. The Hosting Capacity (HC) by circuit is provided for comparison. The Existing HC is the current hosting capacity for each circuit. The Updated HC is the updated hosting capacity as a result of this analysis. The Executed DER, Total Anticipated DER, and Hosting Capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
|  | Total Anticipated DER |  |  |  |  | Hosting Capacity
Circuit | Executed DER | 2021 | 2022 | 2023 | 2024 | 2025 | Existing HC | Updated HC
Hana 41/10277 | 65.75 | 73.7193 | 82.7502 | 91.5763 | 99.985 | 108.2175 | 0 | 181
Hana 41/537 | 105.86 | 118.6909 | 133.2309 | 147.4414 | 160.9797 | 174.2343 | 0 | 229
Hana 41/6528 | 33.15 | 37.168 | 41.7212 | 46.1712 | 50.4107 | 54.5614 | 0 | 116
Huelo 74A/Huelo | 136.32 | 152.8428 | 171.5666 | 189.866 | 207.2998 | 224.3682 | 192 | 370
Kahului 8/4048 | 972.31 | 1090.1598 | 1223.7083 | 1354.2295 | 1478.577 | 1600.3185 | 1420 | 2390
Kahului 8/4049 | 826.355 | 926.5142 | 1040.0155 | 1150.9439 | 1256.6255 | 1360.0921 | 338 | 2200
Kaonoulu/1590 | 3355.572 | 3762.2874 | 4223.181 | 4673.6273 | 5102.7673 | 5522.9132 | 0 | 6000
Kaonoulu/1591 | 907.8686 | 1017.9078 | 1142.6051 | 1264.4758 | 1380.582 | 1494.2549 | 0 | 3000
Kauhikoa 98/1295 | 710.629 | 796.7615 | 894.3676 | 989.7612 | 1080.6427 | 1169.6195 | 1142.91 | 1200
Kihei 35/1384 | 7428.666 | 7890.5415 | 8413.9431 | 8925.4804 | 9412.8219 | 9889.9494 | 1158.9 | 9900
Kihei 35/1473 | 2704.9639 | 3032.8217 | 3404.3532 | 3767.4629 | 4113.3974 | 4452.0817 | 0 | 5656.5
Kihei 35/1515 | 5525.371 | 6195.079 | 6953.9984 | 7695.7147 | 8402.3477 | 9094.1708 | 7610.25 | 9300
Kuau 73/4066 | 624.531 | 700.2279 | 786.0083 | 869.8443 | 949.7148 | 1027.9114 | 551.5 | 1940
Kuihelani 209/1653 | 3717.825 | 4168.4476 | 4679.0974 | 5178.1718 | 5653.64 | 6119.143 | 0 | 7019.36
Kuihelani 209/1708 | 2268.755 | 2483.1387 | 2726.0803 | 2963.5149 | 3189.7189 | 3411.1819 | 0 | 4260
Kula 13/1237 | 2371.867 | 2659.3515 | 2985.1315 | 3303.5269 | 3606.8621 | 3903.8399 | 2658.6 | 4500
Kula 13/1238 | 2419.764 | 2709.5437 | 3037.9248 | 3358.8623 | 3664.6193 | 3963.9681 | 3227 | 5500
Kula Ag Park 55/1322 | 640.75 | 694.1715 | 754.7093 | 813.8748 | 870.2418 | 925.4274 | 448.53 | 1252
Lahaina 34/1223 | 5304.296 | 5599.3472 | 5933.702 | 6260.4778 | 6571.7969 | 6876.5913 | 3078.11 | 6876.6
Lahaina 34/1390 | 2203.74 | 2468.6648 | 2768.88 | 3062.29 | 3341.8216 | 3615.4947 | 0 | 4000
Lahaina 34/1398 | 3868.307 | 4246.2645 | 4674.5694 | 5093.1656 | 5491.9621 | 5882.4004 | 971.6 | 7000
Makawao 12/1235 | 1211.11 | 1339.7229 | 1485.4682 | 1627.9098 | 1763.6139 | 1896.4738 | 1536.8 | 2474.1925
Makawao 12/1236 | 945.622 | 1060.237 | 1190.1199 | 1317.0586 | 1437.993 | 1556.3929 | 1315.9 | 2500
Napili 29/1420 | 1883.551 | 2801.2457 | 2991.2788 | 3177.0043 | 3353.945 | 3527.1772 | 2453.72 | 4252
Onehee 40/4055 | 1066.16 | 1195.385 | 1341.8239 | 1484.9434 | 1621.2933 | 1754.7855 | 1700 | 2000
Paia Mauka 93/4042 | 1056.173 | 1184.1875 | 1329.2547 | 1471.0335 | 1606.1062 | 1738.348 | 521.5 | 2000
Peahi 94/1294 | 1428.25 | 1543.7896 | 1674.7202 | 1802.6828 | 1924.5928 | 2043.9477 | 1456.7 | 2430
Pukalani 17/1282 | 2550.947 | 2857.7129 | 3205.3429 | 3545.0929 | 3868.7726 | 4185.6686 | 2927.3 | 5983.29
Pukalani 17/1308 | 3553.883 | 3984.1719 | 4471.7792 | 4948.3336 | 5402.3469 | 5846.8447 | 5155.9 | 9000
Spreckelsville 92/4043 | 875.23 | 980.1011 | 1098.9419 | 1215.0889 | 1325.7421 | 1434.0762 | 0 | 1450
Waiehu 43/1379 | 3033.344 | 3401.0034 | 3817.6385 | 4224.8294 | 4612.7601 | 4992.5604 | 3922.55 | 5000
Waiinu 36/1493 | 6774.839 | 7595.99 | 8526.526 | 9435.9688 | 10302.3947 | 11150.6617 | 8021.54 | 12000
Wailea 25/1517 | 2259.382 | 2533.2326 | 2843.5627 | 3146.8582 | 3435.8079 | 3718.7016 | 2705.41 | 4389.382
Wailea 25/1518 | 1367.794 | 1533.5788 | 1721.4477 | 1905.058 | 2079.9836 | 2251.2429 | 1632.631 | 4000
Wailuku 3/1290 | 3648.005 | 4090.165 | 4591.2249 | 5080.9268 | 5547.4658 | 6004.2268 | 3242.2 | 6004.23
Wailuku 3/4037 | 731.725 | 820.4144 | 920.9182 | 1019.1437 | 1112.7231 | 1204.3412 | 573.21 | 1300

## Lanai Total DER
Return to Assumptions Summary
Lana‘i Total Anticipated DER and Hosting Capacity by Circuit (kW) - High Forecast
The Total Anticipated DER is the sum of the Executed DER and the Adjusted DER Growth by Circuit. The Executed DER for each circuit is the aggregated program size (kW) of all executed DER programs on that circuit as of December 31, 2020. The Hosting Capacity (HC) by circuit is provided for comparison. The Existing HC is the current hosting capacity for each circuit. The Updated HC is the updated hosting capacity as a result of this analysis. The Executed DER, Total Anticipated DER, and Hosting Capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
|  | Total Anticipated DER |  |  |  |  | Hosting Capacity
Circuit | Executed DER | 2021 | 2022 | 2023 | 2024 | 2025 | Existing HC | Updated HC
Miki Basin PP 302/1208 | 321.425 | 343.4229 | 367.8206 | 423.0153 | 449.0129 | 505.8074 | 386 | 2700
Miki Basin PP 302/1210 | 2140.644 | 2148.2163 | 2156.6147 | 2175.6144 | 2184.5635 | 2204.1139 | 2154 | 3900

## Molokai Total DER
Return to Assumptions Summary
Moloka‘i Total Anticipated DER and Hosting Capacity by Circuit (kW) - High Forecast
The Total Anticipated DER is the sum of the Executed DER and the Adjusted DER Growth by Circuit. The Executed DER for each circuit is the aggregated program size (kW) of all executed DER programs on that circuit as of December 31, 2020. The Hosting Capacity (HC) by circuit is provided for comparison. The Existing HC is the current hosting capacity for each circuit. The Updated HC is the updated hosting capacity as a result of this analysis. The Executed DER, Total Anticipated DER, and Hosting Capacity is shown by circuit (or feeder) in kilowatts (kW) for years 2021-2025.
|  | Total Anticipated DER |  |  |  |  | Hosting Capacity
Circuit | Executed DER | 2021 | 2022 | 2023 | 2024 | 2025 | Existing HC | Updated HC
Palaau PP 81/105A | 817.87 | 930.9529 | 1046.7202 | 1141.3474 | 1248.7258 | 1332.6152 | 1025.5 | 1350
Palaau PP 81/106B | 217.23 | 247.2653 | 278.0137 | 303.1471 | 331.6673 | 353.9487 | 282.2 | 550
Palaau PP 81/109B | 111 | 126.3474 | 142.0592 | 154.9018 | 169.4751 | 180.8604 | 125 | 800
Palaau PP 81/110B | 221.84 | 251.4619 | 281.787 | 306.5745 | 334.7021 | 356.6768 | 212 | 1000
Palaau PP 81/111A | 872.427 | 1242.6384 | 1365.7035 | 1466.2958 | 1580.4431 | 1669.6207 | 823 | 2000

## Summary GNA
Return to Assumptions Summary
Grid Needs Assessment Summary - High Forecast
These tables summarize the Grid Needs Assessment results for all islands. Non-Infrastrucutre Investments indicate circuits where the solution is a modification to existing equipment (e.g. LTC settings change only). Infrastructure Investments indicate circuits where the solution requires infrastructure investments (e.g. circuit phase balancing, new line voltage regulator, etc).
Island | Total Circuits | Violation Type |  | Solution Option
|  | Voltage | Conductor Overload | Non-Infrastructure Investments | Infrastructure Investments
O‘ahu | 32 | 31 | 5 | 15 | 17
Hawai‘i Island | 34 | 34 | - | 32 | 2
Maui Island | 20 | 19 | 2 | 13 | 7
Lana‘i | 2 | 2 | - | - | 2
Moloka‘i | 5 | 5 | - | - | 5
Total (All Islands) | 93 | 91 | 7 | 60 | 33

## Oahu GNA
Return to Assumptions Summary
O‘ahu Grid Needs Assessment - High Forecast
The Grid Needs Assessment shows the grid needs identified for each circuit for the next 5 years (years 2021 through 2025). The Violation Type indicates whether a thermal and/or voltage violation triggers the grid need. The Operating Date indicates the date at which traditional infrastructure must be constructed and energized, in advance of the forecasted grid need to maintain safety and reliability. The Traditional Solution lists the solution identified for mitigation. The Cost Estimate is the estimated cost (dollars) to provide traditional solution identified.
Substation | Circuit | Violation Type | Operating Date | Traditional Solution | Cost Estimate
AIEA 2 | AIEA | Voltage | 2022 | LTC setting change | -
WAILUPE | AINA KOA | Voltage | 2022 | Circuit phase balancing | 14400
KAMILOIKI | ANUU | Voltage | 2023 | LTC setting change | -
KAPAHULU 4 | DIAMOND HEAD | Voltage | 2022 | LTC setting change | -
EWA BEACH 2 | EWA BEACH 3 | Voltage | 2023 | LTC setting change | -
EWA BEACH 2 | EWA BEACH 4 | Voltage | 2023 | LTC setting change | -
KAHALA 2 4KV | FARMERS RD | Voltage, conductor overloading | 2023 | Circuit phase balancing, Install two 3ph line regulators, Reconductoring | 605190.9091
WAIALUA 2 | KAENA PT | Voltage | 2023 | LTC setting change | -
KAHALA 1 4KV | KAHALA | Voltage, conductor overloading | 2022 | Install 3ph line regulator, Reconductoring, new tie switch | 1206916.6667
KEOLU 2 | KAILUA HTS | Voltage | 2025 | LTC setting change | -
KALAMA 1 4KV | KAINALU | Voltage, conductor overloading | 2021 | Dynamic LTC, Install two 1ph line regulators, Reconductoring | 439726.7045
AIKAHI 1 | KALAHEO | Voltage | 2025 | LTC setting change | -
WAIALUA 3 | KAWAILOA | Voltage | 2021 | LTC setting change | -
KAHALA 2 4KV | KILAUEA 4KV | Voltage | 2022 | Circuit phase balancing and Install 3ph line regulator | 213600
KAHALA 2 4KV | KOLOA | Voltage, conductor overloading | 2024 | Circuit phase balancing, Install 3ph line regulator, Reconductoring | 470853.7879
KUILIMA 2 | KUILIMA 1 | Voltage | 2025 | LTC setting change | -
WOODLAWN 2 | LOWREY | Voltage | 2023 | Install two 1ph line regulators | 140000
MAKAKILO 2 | MAKAKILO 2 | Voltage | 2022 | LTC setting change | -
PIIKOI 3 | MANOA-PIIKOI | Voltage | 2024 | Circuit phase balancing | 3600
MAKAHA 2 | MAUKA | Voltage | 2023 | Circuit phase balancing | 3600
MIKILUA 2 | MIKILUA 3 | Voltage | 2023 | Circuit phase balancing | 3600
MIKILUA 2 | MIKILUA 4 | Voltage, transformer overloading | 2021 | Step-down transformer upgrade | 68000
MIKILUA 3 | MIKILUA 5 | Voltage | 2023 | Dynamic LTC | 154000
KALAMA 1 4KV | ONEAWA | Voltage | 2022 | LTC setting change | -
PAUOA 1 | PAUOA 2 | Voltage | 2023 | Circuit phase balancing and partial 4kV-12kV conversion | 610200
PIIKOI 4 | PIIKOI 8 | Conductor overloading | 2022 | Reconductoring | 270000
AHI 2 | PORTLOCK | Voltage | 2024 | LTC setting change | -
WAIALUA 3 | WAIALUA | Voltage | 2022 | LTC setting change | -
WAILUPE | WAILUPE | Voltage | 2023 | Circuit phase balancing | 7200
WAIMANALO BCH 1 | WAIMANALO | Voltage | 2025 | Dynamic LTC | 154000
WAIMEA 1 | WAIMEA 2 | Voltage | 2024 | LTC setting change | -
WAIALAE 1 4KV | WAI-WILHELMINA | Voltage | 2025 | Install two 1ph line regulators | 140000

## Hawaii Island GNA
Return to Assumptions Summary
Hawai‘i Island Grid Needs Assessment - High Forecast
The Grid Needs Assessment shows the grid needs identified for each circuit for the next 5 years (years 2021 through 2025). The Violation Type indicates whether a thermal and/or voltage violation triggers the grid need. The Operating Date indicates the date at which traditional infrastructure must be constructed and energized, in advance of the forecasted grid need to maintain safety and reliability. The Traditional Solution lists the solution identified for mitigation. The Cost Estimate is the estimated cost (dollars) to provide traditional solution identified.
Substation | Circuit | Violation Type | Operating Date | Traditional Solution | Cost Estimate
Captain Cook | Captain Cook 12 | Voltage | 2025 | LTC setting change | -
Halaula | Halaula 1 | Voltage | 2022 | Install two 3ph line regulator | 420000
Hawaiian Paradise Park 2 | Hawaiian Paradise Park 13 | Voltage | 2021 | LTC setting change | -
Hawaiian Paradise Park 2 | Hawaiian Paradise Park 14 | Voltage | 2021 | LTC setting change | -
Honokaa 2 | Honokaa 12 | Voltage | 2021 | LTC setting change | -
Huehue | Huehue 11 | Voltage | 2024 | LTC setting change | -
Kahaluu 1 | Kahaluu 11 | Voltage | 2025 | LTC setting change | -
Kaloko 2 | Kaloko 13 | Voltage | 2025 | LTC setting change | -
Kapua 1 | Kapua 11 | Voltage | 2021 | LTC setting change | -
Kauhale | Kauhale 11 | Voltage | 2021 | LTC setting change | -
Kauhale | Kauhale 12 | Voltage | 2021 | LTC setting change | -
Kaumana | Kaumana 11 | Voltage | 2025 | LTC setting change | -
Kawaihae | Kawaihae 11 | Voltage | 2024 | LTC setting change | -
Kawaihae | Kawaihae 12 | Voltage | 2025 | LTC setting change | -
Keahole Airport | Keahole Airport 11 | Voltage | 2022 | LTC setting change | -
Keahole Airport | Keahole Airport 12 | Voltage | 2025 | LTC setting change | -
Keahole Airport | Keahole Airport 13 | Voltage | 2024 | LTC setting change | -
Komohana 1 | Komohana 12 | Voltage | 2021 | LTC setting change | -
Kuakini 1 | Kuakini 11 | Voltage | 2023 | LTC setting change | -
Kurtistown | Kurtistown 12 | Voltage | 2021 | LTC setting change | -
Laupahoehoe | Laupahoehoe 2 | Voltage | 2022 | LTC setting change | -
Mauna Lani 2 | Mauna Lani 14 | Voltage | 2021 | LTC setting change | -
Namakani Paio | Namakani Paio | Voltage | 2021 | LTC setting change | -
Ookala | Ookala | Voltage | 2021 | LTC setting change | -
Orchid Isle | Orchid Isle 11 | Voltage | 2021 | LTC setting change | -
Orchid Isle | Orchid Isle 12 | Voltage | 2021 | LTC setting change | -
Paauilo | Paauilo 1 | Voltage | 2021 | LTC setting change | -
Panaewa | Panaewa 12 | Voltage | 2021 | LTC setting change | -
Puueo 2 | Puueo 11 | Voltage | 2021 | LTC setting change | -
Puueo 2 | Puueo 12 | Voltage | 2021 | LTC setting change | -
Puuwaawaa | Puuwaawaa 11 | Voltage | 2021 | Install 3ph line regulator | 210000
Waikii | Waikii 12 | Voltage | 2021 | LTC setting change | -
Waikoloa | Waikoloa 12 | Voltage | 2022 | LTC setting change | -
Waipunahina | Waipunahina 11 | Voltage | 2022 | LTC setting change | -

## Maui GNA
Return to Assumptions Summary
Maui Island Grid Needs Assessment - High Forecast
The Grid Needs Assessment shows the grid needs identified for each circuit for the next 5 years (years 2021 through 2025). The Violation Type indicates whether a thermal and/or voltage violation triggers the grid need. The Operating Date indicates the date at which traditional infrastructure must be constructed and energized, in advance of the forecasted grid need to maintain safety and reliability. The Traditional Solution lists the solution identified for mitigation. The Cost Estimate is the estimated cost (dollars) to provide traditional solution identified.
Substation | Circuit | Violation Type | Operating Date | Traditional Solution | Cost Estimate
Huelo | Huelo 74A/Huelo | Voltage | 2024 | Install 1ph line regulator | 70000
Kahului 4 | Kahului 8/4048 | Voltage | 2024 | LTC setting change | -
Kahului 5 | Kahului 8/4049 | Voltage | 2021 | LTC setting change | -
Kauhikoa | Kauhikoa 98/1295 | Voltage | 2025 | LTC setting change | -
Kihei 4 | Kihei 35/1515 | Voltage | 2023 | Install 3ph line regulator | 210000
Kuau | Kuau 73/4066 | Voltage | 2021 | LTC setting change | -
Kuihelani | Kuihelani 209/1653 | Voltage | 2021 | LTC setting change | -
Kuihelani | Kuihelani 209/1708 | Voltage | 2021 | LTC setting change | -
Kula | Kula 13/1237 | Voltage, conductor overloading | 2021 | Reconductor and Install two 3ph line regulators | 2235909.0909
Kula | Kula 13/1238 | Voltage | 2023 | LTC setting change | -
Lahaina 5 | Lahaina 34/1398 | Voltage | 2021 | Install 3ph line regulator | 210000
Makawao | Makawao 12/1236 | Voltage | 2023 | LTC setting change | -
Onehee | Onehee 40/4055 | Conductor overloading | 2025 | Reconductor | 560000
Paia Mauka | Paia Mauka 93/4042 | Voltage | 2021 | Circuit phase balancing | 14400
Peahi | Peahi 94/1294 | Voltage | 2021 | LTC setting change | -
Pukalani 1 | Pukalani 17/1282 | Voltage | 2022 | LTC setting change | -
Spreckelsville | Spreckelsville 92/4043 | Voltage | 2021 | LTC setting change | -
Waiinu 3 | Waiinu 36/1493 | Voltage | 2022 | LTC setting change | -
Wailea 4 | Wailea 25/1517 | Voltage | 2022 | Circuit phase balancing | 14400
Wailea 4 | Wailea 25/1518 | Voltage | 2022 | LTC setting change | -

## Lanai GNA
Return to Assumptions Summary
Lana‘i Island Grid Needs Assessment - High Forecast
The Grid Needs Assessment shows the grid needs identified for each circuit for the next 5 years (years 2021 through 2025). The Violation Type indicates whether a thermal and/or voltage violation triggers the grid need. The Operating Date indicates the date at which traditional infrastructure must be constructed and energized, in advance of the forecasted grid need to maintain safety and reliability. The Traditional Solution lists the solution identified for mitigation. The Cost Estimate is the estimated cost (dollars) to provide traditional solution identified.
Substation | Circuit | Violation Type | Operating Date | Traditional Solution | Cost Estimate
Miki Basin | Miki Basin PP 302/1208 | Voltage | 2023 | Install 3ph line regulator | 252000
Miki Basin | Miki Basin PP 302/1210 | Voltage | 2022 | Install 3ph line regulator | 252000

## Molokai GNA
Return to Assumptions Summary
Moloka‘i Island Grid Needs Assessment - High Forecast
The Grid Needs Assessment shows the grid needs identified for each circuit for the next 5 years (years 2021 through 2025). The Violation Type indicates whether a thermal and/or voltage violation triggers the grid need. The Operating Date indicates the date at which traditional infrastructure must be constructed and energized, in advance of the forecasted grid need to maintain safety and reliability. The Traditional Solution lists the solution identified for mitigation. The Cost Estimate is the estimated cost (dollars) to provide traditional solution identified.
Substation | Circuit | Violation Type | Operating Date | Traditional Solution | Cost Estimate
Palaau | Palaau PP 81/105A | Voltage | 2022 | Install 3ph line regulator | 252000
Palaau | Palaau PP 81/106B | Voltage | 2023 | Install 3ph line regulator | 252000
Palaau | Palaau PP 81/109B | Voltage | 2021 | Install 3ph line regulator | 252000
Palaau | Palaau PP 81/110B | Voltage | 2021 | Install 3ph line regulator | 252000
Palaau | Palaau PP 81/111A | Voltage | 2021 | Install three 3ph line regulator | 756000