## HECO SRD 2_0 URP
Only these columns are transmitted in the CSV File
Parameter Type | RR Label | Required Value | Units | Informational Notes | IEEE Std 1547 2018 Parameter Label (where present) | IEEE Std 1547 2018 Parameter Name (where present) | Description
| NP_NORMAL_OP_CAT | CAT_B | Text | Value: CAT_A/CAT_B | NP_NORMAL_OP_CAT | Normal operating performance category | Normal performance capability (Category A/B SS described in 1.4). If multiple categories are supported, separate with underscores. Cat A_Cat B
| NP_ABNORMAL_OP_CAT | CAT_III | Text | Value: CAT_I/CAT_II/CAT_III | NP_ABNORMAL_OP_CAT | Abnormal operating performance category | Abnormal performance Category (I_ II_ or III_ SS described in 1.4). Where multiple categories are supported, separate with underscores. Cat I_Cat II_Cat III
Permit Service Mode Select | ES_PERMIT_SERVICE-SS | ENABLED | Text |  | ES_PERMIT_SERVICE | Permit service | This function is activated by request from the Area EPS Operator
Enter Service Voltage | ES_V_LOW-SS | 0.88 | V p.u. |  | ES_V_LOW | ES Voltage Low Setting | Per unit value based on NP AC Vnom. (Voltage bSSe). Voltage shall be equal to or greater than default value
| ES_V_HIGH-SS | 1.05 | V p.u. |  | ES_V_HIGH | ES Voltage High Setting | Per unit value based on NP AC Vnom. (Voltage bSSe). Voltage shall be equal to or less than default value
Enter Service Frequency | ES_F_LOW-SS | 59.5 | Hz |  | ES_F_LOW | ES Frequency Low Setting | Frequency shall be equal to or greater than default value. Frequency values shall be reported to 3 decimal places
| ES_F_HIGH-SS | 60.1 | Hz |  | ES_F_HIGH | ES Frequency High Setting | Frequency shall be equal to or less than default value Frequency values shall be reported to 3 decimal places.
Soft-Start Ramp | ES_RANDOMIZED_DELAY-SS | 0 | Text |  | ES_RANDOMIZED_DELAY | ES Randomized Delay | Enter Service Radomized Delay is an optional feature in IEEE Std 1547-2018. When enabled, the delay is a random value between 1 and 1000 seconds
| ES_DELAY-SS | 300 | s |  | ES_DELAY | ES Delay Setting | Minimum Intentional delay before initiating Soft-Start
| ES_RAMP_RATE-SS | 300 | s |  | ES_RAMP_RATE | ES Ramp Rate Setting | Enter Service Soft-Start duration. Time from zero to 100% Prated
Constant Power Factor Mode Select | CONST_PF_MODE_ENABLE-SS | DISABLED | Text |  | CONST_PF_MODE_ENABLE | Constant Power Factor Mode | Constant Power Factor Mode Select
Constant Power Factor Excitation | CONST_PF_EXCITATION-SS | ABS | Text |  | CONST_PF_EXCITATION | Constant Power Factor Excitation | Under or Over Excited
Constant Power Factor | CONST_PF-SS | -0.9 | VAr p.u | absorbing | CONST_PF | Constant Power Factor Absorbing Setting | Per unit based on NP Qmax Abs. Negative signs indicate absorbing VAr
Constant Q Mode Select | CONST_Q_MODE_ENABLE-SS | DISABLED | Text |  | CONST_Q_MODE_ENABLE | Constant Reactive Power Mode Enable | Constant Reactive Power Mode Select
Constant Q | CONST_Q_MODE_EXCITATION-SS | INJ | Text |  | CONST_Q_MODE_EXCITATION | Constant Reactive Power Excitation (not specified in 1547) | Under or Over Excited. This does not exist in 1547 but is needed
| CONST_Q-SS | 0.9 | VAr p.u. |  | CONST_Q | Constant Reactive power setting (see Table 7) | Negative signs indicate absorbing VAr.
Q(V) Mode Select | QV_MODE_ENABLE-SS | ENABLED | Text |  | CONST_Q | Constant Reactive power setting (see Table 7) | Enable_ Disable (0_ 1) Specifed by AEPSO
Q(V) Fixed Vref | QV_VREF-SS | 1.0 | V p.u. |  | QV_VREF | Vref | Per unit value based on NP AC Vnom. (Voltage bSSe).
Q(V) Fixed Vref Mode Select | QV_VREF_AUTO_MODE-SS | DISABLED | Text |  | QV_VREF_AUTO_MODE | Autonomous Vref Adjustment Enable | Enable_ Disable (0_ 1) Specifed by AEPSO
Q(V) Auto Vref Avg Time | QV_VREF_OLRT-SS | 300 | s |  | QV_VREF_OLRT | Vref Adjustment time Constant | Vref time constant in seconds SS specified by the Area EPS Operator
Q(V) Curve Point V2 | QV_CURVE_V2-SS | 0.98 | V p.u. |  | QV_CURVE_V2 | V/Q Curve Point V2 Setting | Undervoltage magnitude where VArs are at minimum. Per unit value based on NP AC Vnom. (Voltage bSSe).
Q(V) Curve Point Q2 | QV_CURVE_Q2-SS | 0% of NP_Q_MAX_INJ | VAr p.u. |  | QV_CURVE_Q2 | V/Q Curve Point Q2 Setting | VArs at V2. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(V) Curve Point V3 | QV_CURVE_V3-SS | 1 | V p.u. |  | QV_CURVE_V3 | V/Q Curve Point V3 Setting | Overvoltage magnitude where VArs are at minimum. Per unit value based on NP AC Vnom. (Voltage bSSe).
Q(V) Curve Point Q3 | QV_CURVE_Q3-SS | 0% of NP_Q_MAX_ABS | VAr p.u. |  | QV_CURVE_Q3 | V/Q Curve Point Q3 Setting | VArs at V3. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(V) Curve Point V1 | QV_CURVE_V1-SS | 0.92 | V p.u. |  | QV_CURVE_V1 | V/Q Curve Point V1 Setting | Undervoltage magnitude where VArs are at maximum. Per unit value based on NP AC Vnom. (Voltage bSSe).
Q(V) Curve Point Q1 | QV_CURVE_Q1-SS | NP_Q_MAX_INJ | VAr p.u. |  | QV_CURVE_Q1 | V/Q Curve Point Q1 Setting | VArs at V1. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(V) Curve Point V4 | QV_CURVE_V4-SS | 1.06 | V p.u. |  | QV_CURVE_V4 | V/Q Curve Point V4 Setting | Overvoltage magnitude where VArs are at minimum. Per unit value based on NP AC Vnom. (Voltage bSSe).
Q(V) Curve Point Q4 | QV_CURVE_Q4-SS | NP_Q_MAX_ABS | VAr p.u. |  | QV_CURVE_Q4 | V/Q Curve Point Q4 Setting | VArs at V4. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(V) OLRT | QV_OLRT-SS | 5 | s |  | QV_OLRT | QV Open Loop Response Time Setting | Volt VAr Open Loop Response time
Q(P) Mode Enable | QP_MODE_ENABLE-SS | DISABLED | Text |  | QP_MODE_ENABLE | Active Power Reactive Power Mode Enable | This function is deactivated by request from the Area EPS Operator
Q(P) Curve Point P3 (Gen) | QP_CURVE_P3_GEN-SS | NP_P_MAX | P p.u. |  | QP_CURVE_P3_GEN | P-Q curve P3 Setting | Maximum Active Power_ Generating. Per unit value based on NP Pmax
Q(P) Curve Point P2 (Gen) | QP_CURVE_P2_GEN-SS | 50% of NP_P_MAX | P p.u. |  | QP_CURVE_P2_GEN | P-Q curve P2P-Q Setting | Medium Active Power_ Generating . Per unit value based on NP Pmax
Q(P) Curve Point P1 (gen) | QP_CURVE_P1_GEN-SS | GREATER OF 20% NP_P_MAX and P_MIN | P p.u. |  | QP_CURVE_P1_GEN | P-Q curve P1 Setting | Lower Active Power_ Generating. Per unit value based on NP Pmax
Q(P) Curve Point P'1 (load) | QP_CURVE_P1_LOAD-SS | 70% of NP_P_MAX_CHARGE | P p.u. |  | QP_CURVE_P1_LOAD | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Lower Active Power_ Absorbing. Per unit value based on NP Pmax Charge
Q(P) Curve Point P'2 (load) | QP_CURVE_P2_LOAD-SS | 80% of NP_P_MAX_CHARGE | P p.u. |  | QP_CURVE_P2_LOAD | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Medium Active Power_ Absorbing. Per unit value based on NP Pmax Charge
Q(P) Curve Point P'3 (load) | QP_CURVE_P3_LOAD-SS | 100% of NP_P_MAX_CHARGE | P p.u. |  | QP_CURVE_P3_LOAD | P-Q curve P3 Setting | Maximum Active Power_ Absorbing. Per unit value based on NP Pmax Charge
Q(P) Curve Point Q3 (gen) | QP_CURVE_Q3_GEN-SS | 100% of NP_Q_MAX_ABS | VAr p.u. |  | QP_CURVE_Q3_GEN | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Maximum Reactive Power while Generating. . Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(P) Curve Point Q2 (gen) | QP_CURVE_Q2_GEN-SS | 100% of NP_Q_MAX_ABS | VAr p.u. |  | QP_CURVE_Q2_GEN | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Medium Reactive Power while Generating. . Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(P) Curve Point Q1 (gen) | QP_CURVE_Q1_GEN-SS | 100% of NP_Q_MAX_ABS | VAr p.u. |  | QP_CURVE_Q1_GEN | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Lower Reactive Power while Generating. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(P) Curve Point Q'1 (load) | QP_CURVE_Q1_LOAD-SS | 100% of NP_Q_MAX_ABS | VAr p.u. |  | QP_CURVE_Q1_LOAD | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Maximum Reactive Power while Absorbing. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(P) Curve Point Q'2 (load) | QP_CURVE_Q2_LOAD-SS | 100% of NP_Q_MAX_ABS | VAr p.u. |  | QP_CURVE_Q2_LOAD | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Medium Reactive Power while Absorbing. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(P) Curve Point Q'3 (load) | QP_CURVE_Q3_LOAD-SS | 100% of NP_Q_MAX_ABS | VAr p.u. |  | QP_CURVE_Q3_LOAD | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Lower Reactive Power while Absorbing. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
P(V) Mode Enable | PV_MODE_ENABLE-SS | ENABLED | Text |  | PV_MODE_ENABLE | Voltage-Active Power Mode Enable | This function is activated by request from the Area EPS Operator
P(V) Curve Point V1 | PV_CURVE_V1-SS | 1.06 | V p.u. |  | PV_CURVE_V1 | PV Curve Point V1 Setting | Upper start voltage for power reduction. Per unit value based on NP AC Vnom. (Voltage bSSe).
P(V) Curve Point P1 | PV_CURVE_P1-SS | 100% of NP_P_MAX | P p.u. |  | PV_CURVE_P1 | PV Curve Point P1 Setting | Active power level at V1. Per unit value based on NP AC Vnom. (Voltage bSSe).
P(V) Curve Point V2 | PV_CURVE_V2-SS | 1.1 | V p.u. |  | PV_CURVE_V2 | PV Curve Point V2 Setting | Upper voltager for maximum power reduction. Per unit value based on NP AC Vnom. (Voltage bSSe).
P(V) Curve Point P2 (gen) | PV_CURVE_P2_GEN-SS | P_MIN | P p.u. |  | PV_CURVE_P2_GEN | PV Curve Point P2 gen Setting | Minimum active power generating at V2_ the lesser of 0.2*Prated or Pmin. Per unit value based on NP Pmax
P(V) Curve Point P'2 (load) | PV_CURVE_P2_LOAD-SS | 0 | P p.u. |  | PV_CURVE_P2_LOAD | PV Curve Point P'2 load Setting | Applicable to DER which can generate and absorb active power. Per unit Value based on NP Pmax Charge. Negative values indicate active power load. P'2 indicates maximum active power absorption
OV2 | OV2_TRIP_V-SS | 1.2 | V p.u. |  | OV2_TRIP_V | HV Trip Curve Point OV2 Setting | Must Trip Magnitude. Per unit value based on NP AC Vnom. (Voltage bSSe).
| OV2_TRIP_T-SS | 0.16 | s |  | OV2_TRIP_T | HV Trip Curve Point OV2 Setting | Must Trip Duration
OV1 | OV1_TRIP_V-SS | 1.1 | V p.u. |  | OV1_TRIP_V | HV Trip Curve Point OV1 Setting | Must Trip Magnitude. Per unit value based on NP AC Vnom. (Voltage bSSe).
| OV1_TRIP_T-SS | 13 | s |  | OV1_TRIP_T | HV Trip Curve Point OV1 Setting | Must Trip Duration
UV1 | UV1_TRIP_V-SS | 0.88 | V p.u. |  | UV1_TRIP_V | LV Curve Trip Point UV1 (see Table 11_ 13) Setting | Must Trip Magnitude. Per unit value based on NP AC Vnom. (Voltage bSSe).
| UV1_TRIP_T-SS | 21 | s |  | UV1_TRIP_T | LV Curve Trip Point UV1 (see Table 11_ 13) Setting | Must Trip Duration
UV2 | UV2_TRIP_V-SS | 0.1 | V p.u. |  | UV2_TRIP_V | LV Curve Trip Point UV2 (see Table 11_ 13) Setting | Must Trip Magnitude. Per unit value based on NP AC Vnom. (Voltage bSSe).
| UV2_TRIP_T-SS | 2 | s |  | UV2_TRIP_T | LV Curve Trip Point UV2 (see Table 11_ 13) Setting | Must Trip Duration
OF2 | OF2_TRIP_F-SS | 65 | Hz |  | OF2_TRIP_F | OF Curve Trip Point OF2 (see Table 19) Setting | Must Trip frequency Magnitude. Frequency values shall be reported to 3 decimal places
| OF2_TRIP_T-SS | 0.16 | s |  | OF2_TRIP_T | OF Curve Trip Point OF2 (see Table 19) Setting | Must Trip Duration
OF1 | OF1_TRIP_F-SS | 63 | Hz |  | OF1_TRIP_F | OF Curve Trip Point OF1 (see Table 19) Setting | Must Trip frequency Magnitude. Frequency values shall be reported to 3 decimal places
| OF1_TRIP_T-SS | 180 | s |  | OF1_TRIP_T | OF Curve Trip Point OF1 (see Table 19) Setting | Must Trip Duration
UF1 | UF1_TRIP_F-SS | 57 | Hz |  | UF1_TRIP_F | UF Curve Trip Point UF1 (see Table 19) Setting | Must Trip frequency Magnitude. Frequency values shall be reported to 3 decimal places
| UF1_TRIP_T-SS | 180 | s |  | UF1_TRIP_T | UF Curve Trip Point UF1 (see Table 19) Setting | Must Trip Duration
UF2 | UF2_TRIP_F-SS | 50 | Hz |  | UF2_TRIP_F | UF Curve Trip Point UF2 (see Table 19) Setting | Must Trip frequency Magnitude. Frequency values shall be reported to 3 decimal places
| UF2_TRIP_T-SS | 0.16 | s |  | UF2_TRIP_T | UF Curve Trip Point UF2 (see Table 19) Setting | Must Trip Duration
P(f )Deadband | PF_DBOF-SS | 0.036 | Hz |  | PF_DBOF | Overfrequency Droop dbOF Setting | Over Frequency deadband offset from nominal frequency in Hz Frequency values shall be reported to 3 decimal places
| PF_DBUF-SS | 0.036 | Hz |  | PF_DBUF | Underfrequency Droop dbUF Setting | Under Frequency deadband offset from nominal frequency in Hz Frequency values shall be reported to 3 decimal places
P(f) Droop Coefficient | PF_KOF-SS | 0.04 | unitless |  | PF_KOF | Overfrequency Droop kOF Setting | Over frequency per unit frequency change corresponding to a 1 per unit power change (frequency droop)
| PF_KUF-SS | 0.04 | unitless |  | PF_KUF | Underfrequency Droop kUF Setting | Under frequency per unit frequency change corresponding to a 1 per unit power change (frequency droop)
P(f) Open Loop Response Time | PF_OLRT-SS | 0.5 | s |  | PF_OLRT | P(f) Open Loop Response Time Setting | Open Loop Response time
UI Mode Select | UI_MODE_ENABLE-SS | ENABLED | Text |  | UI_MODE_ENABLE | N/A—AI is always on in IEEE Std 1547 BUT IEEE Std 1547.1 test says turn it off for some testing | Unintentional Islanding Mode (enabled/disabled). This function is enabled by default, and disabled only by request from the Area EPS Operator.

## Sheet2
IEEE Std 1547-2018 Parameter Name (where present) | IEEE Std 1547-2018 Parameter Label
Active power rating at unity power factor | NP_P_MAX
Active power rating at specified over-excited power factor | NP_P_MAX_OVER_PF
Specified over-excited power factor | NP_OVER_PF
Active power rating at specified under-excited power factor | NP_P_MAX_UNDER_PF
Specified under-excited power factor | NP_UNDER_PF
Apparent power maximum rating | NP_VA_MAX
Normal operating performance category | NP_NORMAL_OP_CAT
Abnormal operating performance category | NP_ABNORMAL_OP_CAT
Intentional island category (optional) | NP_INTENTIONAL_ISLAND_CAT
Reactive power injected maximum rating | NP_Q_MAX_INJ
Reactive power absorbed maximum rating | NP_Q_MAX_ABS
Active power charge maximum rating | NP_P_MAX_CHARGE
Apparent power charge maximum rating | NP_APPARENT_POWER_CHARGE_MAX
AC voltage base—nominal voltage rating(s) | NP_AC_V_NOM
AC voltage maximum rating Maximum | NP_AC_V_MAX
AC voltage minimum rating Minimum | NP_AC_V_MIN
Supported control mode functions | NP_SUPPORTED_MODES
Reactive susceptance (Not specified in IEEE Std 1547) | NP_REACTIVE_SUSCEPTANCE
Not supported in IEEE Std 1547 | NP_REMOTE_METER_RESISTANCE
Not supported in IEEE Std 1547 | NP_REMOTE_METER_REACTANCE
Manufacturer name | NP_MANUFACTURER
Model number | NP_MODEL
Serial number | NP_SERIAL_NUM
Firmware version number | NP_FW_VER
Permit service | ES_PERMIT_SERVICE
ES Voltage Low Setting | ES_V_LOW
ES Voltage High Setting | ES_V_HIGH
ES Frequency Low Setting | ES_F_LOW
ES Frequency High Setting | ES_F_HIGH
ES Randomized Delay | ES_RANDOMIZED_DELAY
ES Delay Setting | ES_DELAY
ES Ramp Rate Setting | ES_RAMP_RATE
Constant Power Factor Mode | CONST_PF_MODE_ENABLE
Constant Power Factor Excitation | CONST_PF_EXCITATION
Constant Power Factor Absorbing Setting | CONST_PF_ABS
Constant Power Factor Absorbing Setting | CONST_PF_INJ
Constant Reactive Power Mode Enable | CONST_Q_MODE_ENABLE
Constant Reactive Power Excitation (not specified in 1547) | CONST_Q_MODE_EXCITATION
Constant Reactive power setting (see Table 7) | CONST_Q
Voltage-Reactive Power Mode Enable | QV_MODE-ENABLE
Vref | QV_VREF
Autonomous Vref Adjustment Enable | QV_VREF_AUTO_MODE
Vref Adjustment time Constant | QV_VREF_OLRT
V/Q Curve Point V2 Setting | QV_CURVE_V2
V/Q Curve Point Q2 Setting | QV_CURVE_Q2
V/Q Curve Point V3 Setting | QV_CURVE_V3
V/Q Curve Point Q3 Setting | QV_CURVE_Q3
V/Q Curve Point V1 Setting | QV_CURVE_V1
V/Q Curve Point Q1 Setting | QV_CURVE_Q1
V/Q Curve Point V4 Setting | QV_CURVE_V4
V/Q Curve Point Q4 Setting | QV_CURVE_Q4
QV Open Loop Response Time Setting | QV_OLRT
Active Power Reactive Power Mode Enable | QP_MODE_ENABLE
P-Q curve P3 Setting | QP_CURVE_P3_GEN
P-Q curve P2P-Q Setting | QP_CURVE_P2_GEN
P-Q curve P1 Setting | QP_CURVE_P1_GEN
P-Q curve P3 Setting | QP_CURVE_P1_LOAD
P-Q curve P3 Setting | QP_CURVE_P2_LOAD
P-Q curve P3 Setting | QP_CURVE_P3_LOAD
P-Q curve P3 Setting | QP_CURVE_Q3_GEN
P-Q curve P3 Setting | QP_CURVE_Q2_GEN
P-Q curve P3 Setting | QP_CURVE_Q1_GEN
P-Q curve P3 Setting | QP_CURVE_Q1_LOAD
P-Q curve P3 Setting | QP_CURVE_Q2_LOAD
P-Q curve P3 Setting | QP_CURVE_Q3_LOAD
QP Open Loop Response Time Setting | QP_OLRT
Voltage-Active Power Mode Enable | PV_MODE_ENABLE
PV Curve Point V1 Setting | PV_CURVE_V1
PV Curve Point P1 Setting | PV_CURVE_P1
PV Curve Point V2 Setting | PV_CURVE_V2
PV Curve Point P2 gen Setting | PV_CURVE_P2_GEN
PV Curve Point P'2 load Setting | PV_CURVE_P2_LOAD
P(V) Open Loop Response time Setting | PV_OLRT
HV Trip Curve Point OV3 Setting | OV3_TRIP_V
HV Trip Curve Point OV3 Setting | OV3_TRIP_T
HV Trip Curve Point OV2 Setting | OV2_TRIP_V
HV Trip Curve Point OV2 Setting | OV2_TRIP_T
HV Trip Curve Point OV1 Setting | OV1_TRIP_V
HV Trip Curve Point OV1 Setting | OV1_TRIP_T
LV Curve Trip Point UV1 (see Table 11_ 13) Setting | UV1_TRIP_V
LV Curve Trip Point UV1 (see Table 11_ 13) Setting | UV1_TRIP_T
LV Curve Trip Point UV2 (see Table 11_ 13) Setting | UV2_TRIP_V
LV Curve Trip Point UV2 (see Table 11_ 13) Setting | UV2_TRIP_T
LV Curve Trip Point UV3 (see Table 11_ 13) Setting | UV3_TRIP_V
LV Curve Trip Point UV3 (see Table 11_ 13) Setting | UV3_TRIP_T
OF Curve Trip Point OF2 (see Table 19) Setting | OF2_TRIP_F
OF Curve Trip Point OF2 (see Table 19) Setting | OF2_TRIP_T
OF Curve Trip Point OF1 (see Table 19) Setting | OF1_TRIP_F
OF Curve Trip Point OF1 (see Table 19) Setting | OF1_TRIP_T
UF Curve Trip Point UF1 (see Table 19) Setting | UF1_TRIP_F
UF Curve Trip Point UF1 (see Table 19) Setting | UF1_TRIP_T
UF Curve Trip Point UF2 (see Table 19) Setting | UF2_TRIP_F
UF Curve Trip Point UF2 (see Table 19) Setting | UF2_TRIP_T
frequency-Active Power Mode Enable | PF_MODE_ENABLE
Overfrequency Droop dbOF Setting | PF_DBOF
Underfrequency Droop dbUF Setting | PF_DBUF
Overfrequency Droop kOF Setting | PF_KOF
Underfrequency Droop kUF Setting | PF_KUF
P(f) Open Loop Response Time Setting | PF_OLRT
N/A—AI is always on in IEEE Std 1547 BUT IEEE Std 1547.1 test says turn it off for some testing | UI_MODE_ENABLE
See IEEE Std 1547-2018 4.11.1 | EMC_IMMUN_LEVEL