## HECO SRD 2_0 CSV File Example
Only these columns are transmitted in the CSV File
Parameter Type | RR Label | Required Value | Units | Informational Notes | IEEE Std 1547 2018 Parameter Label (where present) | IEEE Std 1547 2018 Parameter Name (where present) | Description
| NP_NORMAL_OP_CAT | CAT_B | Text | Value: CAT_A/CAT_B | NP_NORMAL_OP_CAT | Normal operating performance category | Normal performance capability (Category A/B as described in 1.4). If multiple categories are supported, separate with underscores. Cat A_Cat B
| NP_ABNORMAL_OP_CAT | CAT_III | Text | Value: CAT_I/CAT_II/CAT_III | NP_ABNORMAL_OP_CAT | Abnormal operating performance category | Abnormal performance Category (I_ II_ or III_ as described in 1.4). Where multiple categories are supported, separate with underscores. Cat I_Cat II_Cat III
| NP_INTENTIONAL_ISLAND_CAT | UNCAT-INT_ISLAND_CAP-BLACK_START-ISOCH | Text | Value: UNCAT/INT_ISLAND_CAP/BLACK_START/ISOCH | NP_INTENTIONAL_ISLAND_CAT | Intentional island category (optional) | Intentional islanding Category (as described in 8.2.8). If mulltiple categories are supported separate with underscores. Uncat_Int Island Cap_Black Start_Isoch
| NP_P_MAX |  |  |  | NP_P_MAX | Active power rating at unity power factor
| NP_P_MAX_CHARGE |  |  |  | NP_P_MAX_CHARGE | Active power charge maximum rating
| NP_Q_MAX_INJ | enter value | kVAr | 44% of kVA rating in kVAr | NP_Q_MAX_INJ | Reactive power injected maximum rating | Maximum injected reactive power rating in kilovolt-amperes reactive
| NP_Q_MAX_ABS | enter value | kVAr | 44% of kVA rating in kVAr | NP_Q_MAX_ABS | Reactive power absorbed maximum rating | Maximum absorbed reactive power rating in kilovolt-amperes reactive
| NP_SUPPORTED_MODES | CONST_PF-QV-QP-PV-PF | Text | Value: CONST_PF/CONST_Q/QV/QP/PV/PF | NP_SUPPORTED_MODES | Supported control mode functions | Indication of support for each control mode function separated by underscores. Const PF_P(V)_Q(V)_Q(P)_P(V)_P(f)
| NP_INTENTIONAL_ISLAND_CAT-AS | UNCAT-INT_ISLAND_CAP-BLACK_START-ISOCH | Text | Value: UNCAT/INT_ISLAND_CAP/BLACK_START/ISOCH | NP_INTENTIONAL_ISLAND_CAT | Intentional island category (optional) | Intentional islanding Category (as described in 8.2.8). If mulltiple categories are supported, separate with underscores. Uncat_Int Island Cap_Black Start_Isoch
Permit Service Mode Select | ES_PERMIT_SERVICE-AS | ENABLED | Text | Required Tested Values: ENABLED/DISABLED | ES_PERMIT_SERVICE | Permit service | This function is activated by request from the Area EPS Operator
Enter Service Voltage | ES_V_LOW-SR-MIN | 0.88 | V p.u. |  | ES_V_LOW | ES Voltage Low Setting | Per unit value based on NP AC Vnom. (Voltage base). Voltage shall be equal to or greater than default value
| ES_V_LOW-SR-MAX | 0.95 | V p.u. |  | ES_V_LOW | ES Voltage Low Setting | Per unit value based on NP AC Vnom. (Voltage base). Voltage shall be equal to or greater than default value
| ES_V_HIGH-SR-MIN | 1.05 | V p.u. |  | ES_V_HIGH | ES Voltage High Setting | Per unit value based on NP AC Vnom. (Voltage base). Voltage shall be equal to or less than default value
| ES_V_HIGH-SR-MAX | 1.06 | V p.u. |  | ES_V_HIGH | ES Voltage High Setting | Per unit value based on NP AC Vnom. (Voltage base). Voltage shall be equal to or less than default value
Enter Service Frequency | ES_F_LOW-SR-MIN | 59 | Hz |  | ES_F_LOW | ES Frequency Low Setting | Frequency shall be equal to or greater than default value. Frequency values shall be reported to 3 decimal places
| ES_F_LOW-SR-MAX | 59.9 | Hz |  | ES_F_LOW | ES Frequency Low Setting | Frequency shall be equal to or greater than default value. Frequency values shall be reported to 3 decimal places
| ES_F_HIGH-SR-MIN | 60.1 | Hz |  | ES_F_HIGH | ES Frequency High Setting | Frequency shall be equal to or less than default value. Frequency values shall be reported to 3 decimal places
| ES_F_HIGH-SR-MAX | 61 | Hz |  | ES_F_HIGH | ES Frequency High Setting | Frequency shall be equal to or less than default value Frequency values shall be reported to 3 decimal places.
Soft-Start Ramp | ES_RANDOMIZED_DELAY-AS | DISABLED | Text | Required Tested Value: DISABLED | ES_RANDOMIZED_DELAY | ES Randomized Delay | Enter Service Radomized Delay is an optional feature in IEEE Std 1547-2018. When enabled, the delay is a random value between 1 and 1000 seconds
| ES_DELAY-SR-MIN | 0 | s |  | ES_DELAY | ES Delay Setting | Minimum Intentional delay before initiating Soft-Start
| ES_DELAY-SR-MAX | 600 | s |  | ES_DELAY | ES Delay Setting | Minimum Intentional delay before initiating Soft-Start
| ES_RAMP_RATE-SR-MIN | 0.1 | %/s |  | ES_RAMP_RATE | ES Ramp Rate Setting | Enter Service Soft-Start duration. Time from zero to 100% Prated
| ES_RAMP_RATE-SR-MAX | 100 | %/s |  | ES_RAMP_RATE | ES Ramp Rate Setting | Enter Service Soft-Start duration. Time from zero to 100% Prated
Constant Power Factor Mode Select | CONST_PF_MODE_ENABLE-AS | ENABLED | Text | Required Tested Values: ENABLED/DISABLED | CONST_PF_MODE_ENABLE | Constant Power Factor Mode | Constant Power Factor Mode Select
Constant Power Factor Excitation | CONST_PF_EXCITATION-AS | INJ | Text | Required Tested Values: INJ/ABS | CONST_PF_EXCITATION | Constant Power Factor Excitation | Under or Over Excited
Constant Power Factor | CONST_PF_ABS-SR-MIN | 0.9 | VAr p.u |  | CONST_PF_ABS | Constant Power Factor Absorbing Setting | Per unit based on NP Qmax Abs. Negative signs should not be used but if present indicate absorbing VAr
| CONST_PF_ABS-SR-MAX | 1 | VAr p.u |  | CONST_PF_ABS | Constant Power Factor Absorbing Setting | Per unit based on NP Qmax Abs. Negative signs should not be used but if present indicate absorbing VAr
| CONST_PF_INJ-SR-MIN | 0.9 | VAr p.u |  | CONST_PF_INJ | Constant Power Factor Absorbing Setting | Per unit based on NP Qmax Inj. Positive signs should not be used but if present indicate injecting VAr
| CONST_PF_INJ-SR-MAX | 1 | VAr p.u |  | CONST_PF_INJ | Constant Power Factor Absorbing Setting | Per unit based on NP Qmax Inj. Positive signs should not be used but if present indicate injecting VAr
| CONST_PF_OLRT-SR-MIN | 10 | s |  |  |  | Maximum response time to maintain constant power factor
| CONST_PF_OLRT-SR-MAX | 10 | s |  |  |  | Maximum Response Time to maintain constant power factor
Constant Q Mode Select | CONST_Q_MODE_ENABLE-AS | ENABLED | Text | Required Tested Values: ENABLED/DISABLED | CONST_Q_MODE_ENABLE | Constant Reactive Power Mode Enable | Constant Reactive Power Mode Select
Constant Q OLRT | CONST_Q_MODE_EXCITATION-AS | INJ | Text | Required Tested Values: INJ/ABS | CONST_Q_MODE_EXCITATION | Constant Reactive Power Excitation (not specified in 1547) | Under or Over Excited. This does not exist in 1547 but is needed
| CONST_Q_ABS-SR-MAX | NP_Q_MAX_ABS | VAr p.u. |  | CONST_Q | Constant Reactive power setting (see Table 7) | Absorbing Reactive Power (maximum RofA) Per unit value based on NP Qmax Abs. Negative signs should not be used but if present indicate absorbing VAr.
| CONST_Q_ABS-SR-MIN | 0 | VAr p.u. |  | CONST_Q | Constant Reactive power setting (see Table 7) | Injecting Reactive Power (minimum RofA) Per unit value based on NP Qmax Inj. Positive signs should not be used but if present indicate Injecting VAr.
| CONST_Q_INJ-SR-MAX | NP_Q_MAX_INJ | VAr p.u. |  | CONST_Q | Constant Reactive power setting (see Table 7) | Injecting Reactive Power (maximum RofA) Per unit value based on NP Qmax Inj. Positive signs should not be used but if present indicate Injecting VAr.
| CONST_Q_INJ-SR-MIN | 0 | VAr p.u. |  | CONST_Q | Constant Reactive power setting (see Table 7)
| CONST_Q_OLRT-SR-MIN | 10 | s |  | CONST_Q | Constant Reactive power setting (see Table 7) | Maximum Response Time to maintain constant reactive power
| CONST_Q_OLRT-SR-MAX | 10 | s |  | CONST_Q | Constant Reactive power setting (see Table 7) | Maximum Response Time to maintain constant reactive power
Q(V) Fixed Vref Mode Select | QV_MODE_ENABLE-AS | ENABLED | Text | Required Tested Values: ENABLED/DISABLED | CONST_Q | Constant Reactive power setting (see Table 7) | Enable_ Disable (0_ 1) Specifed by AEPSO
Q(V) Fixed Vref | QV_VREF-SR-MIN | 0.95 | V p.u. |  | QV_VREF | Vref | Per unit value based on NP AC Vnom. (Voltage base).
| QV_VREF-SR-MAX | 1.05 | V p.u. |  | QV_VREF | Vref | Per unit value based on NP AC Vnom. (Voltage base).
Q(V) Mode Select | QV_VREF_AUTO_MODE-AS | ENABLED | Text | Required Tested Values: ENABLED/DISABLED | QV_VREF_AUTO_MODE | Autonomous Vref Adjustment Enable | Enable_ Disable (0_ 1) Specifed by AEPSO
Q(V) Auto Vref Avg Time | QV_VREF_OLRT-SR-MIN | 300 | s |  | QV_VREF_OLRT | Vref Adjustment time Constant | Vref time constant in seconds as specified by the Area EPS Operator
| QV_VREF_OLRT-SR-MAX | 5000 | s |  | QV_VREF_OLRT | Vref Adjustment time Constant | Vref time constant in seconds as specified by the Area EPS Operator
Q(V) Curve Point V2 | QV_CURVE_V2-SR-MIN | 0.92 | V p.u. |  | QV_CURVE_V2 | V/Q Curve Point V2 Setting | Undervoltage magnitude where VArs are at minimum. Per unit value based on NP AC Vnom. (Voltage base).
| QV_CURVE_V2-SR-MAX | 1.05 | V p.u. |  | QV_CURVE_V2 | V/Q Curve Point V2 Setting | Undervoltage magnitude where VArs are at minimum. Per unit value based on NP AC Vnom. (Voltage base).
Q(V) Curve Point Q2 | QV_CURVE_Q2-SR-MIN | 100% of NP_Q_MAX_ABS | VAr p.u. |  | QV_CURVE_Q2 | V/Q Curve Point Q2 Setting | VArs at V2. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
| QV_CURVE_Q2-SR-MAX | 100% of NP_Q_MAX_INJ | VAr p.u. |  | QV_CURVE_Q2 | V/Q Curve Point Q2 Setting | VArs at V2. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(V) Curve Point V3 | QV_CURVE_V3-SR-MIN | 0.95 | V p.u. |  | QV_CURVE_V3 | V/Q Curve Point V3 Setting | Overvoltage magnitude where VArs are at minimum. Per unit value based on NP AC Vnom. (Voltage base).
| QV_CURVE_V3-SR-MAX | 1.08 | V p.u. |  | QV_CURVE_V3 | V/Q Curve Point V3 Setting | Overvoltage magnitude where VArs are at minimum. Per unit value based on NP AC Vnom. (Voltage base).
Q(V) Curve Point Q3 | QV_CURVE_Q3-SR-MIN | 100% of NP_Q_MAX_ABS | VAr p.u. |  | QV_CURVE_Q3 | V/Q Curve Point Q3 Setting | VArs at V3. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
| QV_CURVE_Q3-SR-MAX | 100% of NP_Q_MAX_INJ | VAr p.u. |  | QV_CURVE_Q3 | V/Q Curve Point Q3 Setting | VArs at V3. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(V) Curve Point V1 | QV_CURVE_V1-SR-MIN | 0.77 | V p.u. |  | QV_CURVE_V1 | V/Q Curve Point V1 Setting | Undervoltage magnitude where VArs are at maximum. Per unit value based on NP AC Vnom. (Voltage base).
| QV_CURVE_V1-SR-MAX | 1.03 | V p.u. |  | QV_CURVE_V1 | V/Q Curve Point V1 Setting | Undervoltage magnitude where VArs are at maximum. Per unit value based on NP AC Vnom. (Voltage base).
Q(V) Curve Point Q1 | QV_CURVE_Q1-SR-MIN | 0% of NP_Q_MAX_INJ | VAr p.u. |  | QV_CURVE_Q1 | V/Q Curve Point Q1 Setting | VArs at V1. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
| QV_CURVE_Q1-SR-MAX | 100% of NP_Q_MAX_INJ | VAr p.u. |  | QV_CURVE_Q1 | V/Q Curve Point Q1 Setting | VArs at V1. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(V) Curve Point V4 | QV_CURVE_V4-SR-MIN | 0.97 | V p.u. |  | QV_CURVE_V4 | V/Q Curve Point V4 Setting | Overvoltage magnitude where VArs are at minimum. Per unit value based on NP AC Vnom. (Voltage base).
| QV_CURVE_V4-SR-MAX | 1.23 | V p.u. |  | QV_CURVE_V4 | V/Q Curve Point V4 Setting | Overvoltage magnitude where VArs are at minimum. Per unit value based on NP AC Vnom. (Voltage base).
Q(V) Curve Point Q4 | QV_CURVE_Q4-SR-MIN | 100% of NP_Q_MAX_ABS | VAr p.u. |  | QV_CURVE_Q4 | V/Q Curve Point Q4 Setting | VArs at V4. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
| QV_CURVE_Q4-SR-MAX | 0% of NP_Q_MAX_ABS | VAr p.u. |  | QV_CURVE_Q4 | V/Q Curve Point Q4 Setting | VArs at V4. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(V) OLRT | QV_OLRT-SR-MIN | 1 | s |  | QV_OLRT | QV Open Loop Response Time Setting | Volt VAr Open Loop Response time
| QV_OLRT-SR-MAX | 90 | s |  | QV_OLRT | QV Open Loop Response Time Setting | Volt VAr Open Loop Response time
Q(P) Mode Enable | QP_MODE_ENABLE-AS | ENABLED | Text | Required Tested Values: ENABLED/DISABLED | QP_MODE_ENABLE | Active Power Reactive Power Mode Enable | This function is deactivated by request from the Area EPS Operator
Q(P) Curve Point P3 (Gen) | QP_CURVE_P3_GEN-SR-MIN | 50% of NP_P_MAX | P p.u. |  | QP_CURVE_P3_GEN | P-Q curve P3 Setting | Maximum Active Power_ Generating. Per unit value based on NP Pmax
| QP_CURVE_P3_GEN-SR-MAX | 100% of NP_P_MAX | P p.u. |  | QP_CURVE_P3_GEN | P-Q curve P3 Setting | Maximum Active Power_ Generating. Per unit value based on NP Pmax
Q(P) Curve Point P2 (Gen) | QP_CURVE_P2_GEN-SR-MIN | 40% of NP_P_MAX | P p.u. |  | QP_CURVE_P2_GEN | P-Q curve P2P-Q Setting | Medium Active Power_ Generating . Per unit value based on NP Pmax
| QP_CURVE_P2_GEN-SR-MAX | 80% of NP_P_MAX | P p.u. |  | QP_CURVE_P2_GEN | P-Q curve P2P-Q Setting | Medium Active Power_ Generating. Per unit value based on NP Pmax
Q(P) Curve Point P1 (gen) | QP_CURVE_P1_GEN-SR-MIN | P_MIN | P p.u. |  | QP_CURVE_P1_GEN | P-Q curve P1 Setting | Lower Active Power_ Generating. Per unit value based on NP Pmax
| QP_CURVE_P1_GEN-SR-MAX | 70% of NP_P_MAX | P p.u. |  | QP_CURVE_P1_GEN | P-Q curve P1 Setting | Lower Active Power_ Generating. Per unit value based on NP Pmax
Q(P) Curve Point P'1 (load) | QP_CURVE_P1_LOAD-SR-MIN | 70% of NP_P_MAX_CHARGE | P p.u. |  | QP_CURVE_P1_LOAD | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Lower Active Power_ Absorbing. Per unit value based on NP Pmax Charge
| QP_CURVE_P1_LOAD-SR-MAX | P_MIN_CHARGE | P p.u. |  | QP_CURVE_P1_LOAD | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Lower Active Power_ Absorbing. Per unit value based on NP Pmax Charge
Q(P) Curve Point P'2 (load) | QP_CURVE_P2_LOAD-SR-MIN | 80% of NP_P_MAX_CHARGE | P p.u. |  | QP_CURVE_P2_LOAD | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Medium Active Power_ Absorbing. Per unit value based on NP Pmax Charge
| QP_CURVE_P2_LOAD-SR-MAX | 40% of NP_P_MAX_CHARGE | P p.u. |  | QP_CURVE_P2_LOAD | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Medium Active Power_ Absorbing. Per unit value based on NP Pmax Charge
Q(P) Curve Point P'3 (load) | QP_CURVE_P3_LOAD-SR-MIN | 100% of NP_P_MAX_CHARGE | P p.u. |  | QP_CURVE_P3_LOAD | P-Q curve P3 Setting | Maximum Active Power_ Absorbing. Per unit value based on NP Pmax Charge
| QP_CURVE_P3_LOAD-SR-MAX | 50% of NP_P_MAX_CHARGE | P p.u. |  | QP_CURVE_P3_LOAD | P-Q curve P3 Setting | Maximum Active Power_ Absorbing. Per unit value based on NP Pmax Charge
Q(P) Curve Point Q3 (gen) | QP_CURVE_Q3_GEN-SR-MIN | 100% of NP_Q_MAX_ABS | VAr p.u. |  | QP_CURVE_Q3_GEN | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Maximum Reactive Power while Generating. . Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
| QP_CURVE_Q3_GEN-SR-MAX | 100% of NP_Q_MAX_INJ | VAr p.u. |  | QP_CURVE_Q3_GEN | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Maximum Reactive Power while Generating. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(P) Curve Point Q2 (gen) | QP_CURVE_Q2_GEN-SR-MIN | 100% of NP_Q_MAX_ABS | VAr p.u. |  | QP_CURVE_Q2_GEN | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Medium Reactive Power while Generating. . Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
| QP_CURVE_Q2_GEN-SR-MAX | 100% of NP_Q_MAX_INJ | VAr p.u. |  | QP_CURVE_Q2_GEN | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Medium Reactive Power while Generating. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(P) Curve Point Q1 (gen) | QP_CURVE_Q1_GEN-SR-MIN | 100% of NP_Q_MAX_ABS | VAr p.u. |  | QP_CURVE_Q1_GEN | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Lower Reactive Power while Generating. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
| QP_CURVE_Q1_GEN-SR-MAX | 100% of NP_Q_MAX_INJ | VAr p.u. |  | QP_CURVE_Q1_GEN | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Lower Reactive Power while Generating. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(P) Curve Point Q'1 (load) | QP_CURVE_Q1_LOAD-SR-MIN | 100% of NP_Q_MAX_ABS | VAr p.u. |  | QP_CURVE_Q1_LOAD | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Maximum Reactive Power while Absorbing. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
| QP_CURVE_Q1_LOAD-SR-MAX | 100% of NP_Q_MAX_INJ | VAr p.u. |  | QP_CURVE_Q1_LOAD | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Maximum Reactive Power while Absorbing. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(P) Curve Point Q'2 (load) | QP_CURVE_Q2_LOAD-SR-MIN | 100% of NP_Q_MAX_ABS | VAr p.u. |  | QP_CURVE_Q2_LOAD | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Medium Reactive Power while Absorbing. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
| QP_CURVE_Q2_LOAD-SR-MAX | 100% of NP_Q_MAX_INJ | VAr p.u. |  | QP_CURVE_Q2_LOAD | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Medium Reactive Power while Absorbing. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(P) Curve Point Q'3 (load) | QP_CURVE_Q3_LOAD-SR-MIN | 100% of NP_Q_MAX_ABS | VAr p.u. |  | QP_CURVE_Q3_LOAD | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Lower Reactive Power while Absorbing. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
| QP_CURVE_Q3_LOAD-SR-MAX | 100% of NP_Q_MAX_INJ | VAr p.u. |  | QP_CURVE_Q3_LOAD | P-Q curve P3 Setting [likely errant in 1547.1-2020] | Lower Reactive Power while Absorbing. Per unit value based on NP Qmax Abs or NP Qmax Inj. Negative signs should not be used but if present indicate absorbing VAr.
Q(P) OLRT | QP_OLRT-SR-MIN | 10 | s |  | QP_OLRT | QP Open Loop Response Time Setting | Q(P) Response Time Min
| QP_OLRT-SR-MAX | 10 | s |  | QP_OLRT | QP Open Loop Response Time Setting | Q(P) Response Time Max
P(V) Mode Enable | PV_MODE_ENABLE-AS | ENABLED | Text | Required Tested Values: ENABLED/DISABLED | PV_MODE_ENABLE | Voltage-Active Power Mode Enable | This function is activated by request from the Area EPS Operator
P(V) Curve Point V1 | PV_CURVE_V1-SR-MIN | 1.05 | V p.u. |  | PV_CURVE_V1 | PV Curve Point V1 Setting | Upper start voltage for power reduction. Per unit value based on NP AC Vnom. (Voltage base).
| PV_CURVE_V1-SR-MAX | 1.09 | V p.u. |  | PV_CURVE_V1 | PV Curve Point V1 Setting | Upper start voltage for power reduction. Per unit value based on NP AC Vnom. (Voltage base).
P(V) Curve Point P1 | PV_CURVE_P1-SR-MIN | 100% of NP_P_MAX | P p.u. |  | PV_CURVE_P1 | PV Curve Point P1 Setting | Active power level at V1. Per unit value based on NP AC Vnom. (Voltage base).
| PV_CURVE_P1-SR-MAX | 100% of NP_P_MAX | P p.u. |  | PV_CURVE_P1 | PV Curve Point P1 Setting | Active power level at V1. Per unit value based on NP AC Vnom. (Voltage base).
P(V) Curve Point V2 | PV_CURVE_V2-SR-MIN | 1.06 | V p.u. |  | PV_CURVE_V2 | PV Curve Point V2 Setting | Upper voltager for maximum power reduction. Per unit value based on NP AC Vnom. (Voltage base).
| PV_CURVE_V2-SR-MAX | 1.1 | V p.u. |  | PV_CURVE_V2 | PV Curve Point V2 Setting | Upper voltager for maximum power reduction. Per unit value based on NP AC Vnom. (Voltage base).
P(V) Curve Point P2 (gen) | PV_CURVE_P2_GEN-SR-MIN | P_MIN | P p.u. |  | PV_CURVE_P2_GEN | PV Curve Point P2 gen Setting | Minimum active power generating at V2_ the lesser of 0.2*Prated or Pmin. Per unit value based on NP Pmax
| PV_CURVE_P2_GEN-SR-MAX | NP_P_MAX | P p.u. |  | PV_CURVE_P2_GEN | PV Curve Point P2 gen Setting | Minimum active power generating at V2_ the lesser of 0.2*Prated or Pmin. Per unit value based on NP Pmax
P(V) Curve Point P'2 (load) | PV_CURVE_P2_LOAD-SR-MIN | 0 | P p.u. |  | PV_CURVE_P2_LOAD | PV Curve Point P'2 load Setting | Applicable to DER which can generate and absorb active power. Per unit Value based on NP Pmax Charge. Negative values indicate active power load. P'2 indicates maximum active power absorption
| PV_CURVE_P2_LOAD-SR-MAX | 100% of NP_P_MAX_CHARGE | P p.u. |  | PV_CURVE_P2_LOAD | PV Curve Point P'2 load Setting | Applicable to DER which can generate and absorb active power. Per unit Value based on NP Pmax Charge. Negative values indicate active power load. P'2 indicates maximum active power absorption
P(V) OLRT | PV_OLRT-SR-MIN | 0.5 | s |  | PV_OLRT | P(V) Open Loop Response time Setting | P(V) Open Loop Response Time Min
| PV_OLRT-SR-MAX | 60 | s |  | PV_OLRT | P(V) Open Loop Response time Setting | P(V) Open Loop Response Respone Time Max
OV2 | OV2_TRIP_V-SR-MIN | 1.2 | V p.u. |  | OV2_TRIP_V | HV Trip Curve Point OV2 Setting | Must Trip Magnitude. Per unit value based on NP AC Vnom. (Voltage base).
| OV2_TRIP_V-SR-MAX | 1.2 | V p.u. |  | OV2_TRIP_V | HV Trip Curve Point OV2 Setting | Must Trip Magnitude. Per unit value based on NP AC Vnom. (Voltage base).
| OV2_TRIP_T-SR-MIN | 0.16 | s |  | OV2_TRIP_T | HV Trip Curve Point OV2 Setting | Must Trip Duration
| OV2_TRIP_T-SR-MAX | 0.16 | s |  | OV2_TRIP_T | HV Trip Curve Point OV2 Setting | Must Trip Duration
OV1 | OV1_TRIP_V-SR-MIN | 1.1 | V p.u. |  | OV1_TRIP_V | HV Trip Curve Point OV1 Setting | Must Trip Magnitude. Per unit value based on NP AC Vnom. (Voltage base).
| OV1_TRIP_V-SR-MAX | 1.2 | V p.u. |  | OV1_TRIP_V | HV Trip Curve Point OV1 Setting | Must Trip Magnitude. Per unit value based on NP AC Vnom. (Voltage base).
| OV1_TRIP_T-SR-MIN | 1 | s |  | OV1_TRIP_T | HV Trip Curve Point OV1 Setting | Must Trip Duration
| OV1_TRIP_T-SR-MAX | 13 | s |  | OV1_TRIP_T | HV Trip Curve Point OV1 Setting | Must Trip Duration
UV1 | UV1_TRIP_V-SR-MIN | 0 | V p.u. |  | UV1_TRIP_V | LV Curve Trip Point UV1 (see Table 11_ 13) Setting | Must Trip Magnitude. Per unit value based on NP AC Vnom. (Voltage base).
| UV1_TRIP_V-SR-MAX | 0.88 | V p.u. |  | UV1_TRIP_V | LV Curve Trip Point UV1 (see Table 11_ 13) Setting | Must Trip Magnitude. Per unit value based on NP AC Vnom. (Voltage base).
| UV1_TRIP_T-SR-MIN | 2 | s | Updated 1547a-2020 value | UV1_TRIP_T | LV Curve Trip Point UV1 (see Table 11_ 13) Setting | Must Trip Duration
| UV1_TRIP_T-SR-MAX | 50 | s |  | UV1_TRIP_T | LV Curve Trip Point UV1 (see Table 11_ 13) Setting | Must Trip Duration
UV2 | UV2_TRIP_V-SR-MIN | 0 | V p.u. |  | UV2_TRIP_V | LV Curve Trip Point UV2 (see Table 11_ 13) Setting | Must Trip Magnitude. Per unit value based on NP AC Vnom. (Voltage base).
| UV2_TRIP_V-SR-MAX | 0.5 | V p.u. |  | UV2_TRIP_V | LV Curve Trip Point UV2 (see Table 11_ 13) Setting | Must Trip Magnitude. Per unit value based on NP AC Vnom. (Voltage base).
| UV2_TRIP_T-SR-MIN | 0.16 | s | Updated 1547a-2020 value | UV2_TRIP_T | LV Curve Trip Point UV2 (see Table 11_ 13) Setting | Must Trip Duration
| UV2_TRIP_T-SR-MAX | 21 | s |  | UV2_TRIP_T | LV Curve Trip Point UV2 (see Table 11_ 13) Setting | Must Trip Duration
OF2 | OF2_TRIP_F-SR-MIN | 61.8 | Hz |  | OF2_TRIP_F | OF Curve Trip Point OF2 (see Table 19) Setting | Must Trip frequency Magnitude. Frequency values shall be reported to 3 decimal places
| OF2_TRIP_F-SR-MAX | 66 | Hz |  | OF2_TRIP_F | OF Curve Trip Point OF2 (see Table 19) Setting | Must Trip frequency Magnitude. Frequency values shall be reported to 3 decimal places
| OF2_TRIP_T-SR-MIN | 0.16 | s |  | OF2_TRIP_T | OF Curve Trip Point OF2 (see Table 19) Setting | Must Trip Duration
| OF2_TRIP_T-SR-MAX | 1000 | s |  | OF2_TRIP_T | OF Curve Trip Point OF2 (see Table 19) Setting | Must Trip Duration
OF1 | OF1_TRIP_F-SR-MIN | 61 | Hz |  | OF1_TRIP_F | OF Curve Trip Point OF1 (see Table 19) Setting | Must Trip frequency Magnitude. Frequency values shall be reported to 3 decimal places
| OF1_TRIP_F-SR-MAX | 66 | Hz |  | OF1_TRIP_F | OF Curve Trip Point OF1 (see Table 19) Setting | Must Trip frequency Magnitude. Frequency values shall be reported to 3 decimal places
| OF1_TRIP_T-SR-MIN | 180 | s |  | OF1_TRIP_T | OF Curve Trip Point OF1 (see Table 19) Setting | Must Trip Duration
| OF1_TRIP_T-SR-MAX | 1000 | s |  | OF1_TRIP_T | OF Curve Trip Point OF1 (see Table 19) Setting | Must Trip Duration
UF1 | UF1_TRIP_F-SR-MIN | 50 | Hz |  | UF1_TRIP_F | UF Curve Trip Point UF1 (see Table 19) Setting | Must Trip frequency Magnitude. Frequency values shall be reported to 3 decimal places
| UF1_TRIP_F-SR-MAX | 59 | Hz |  | UF1_TRIP_F | UF Curve Trip Point UF1 (see Table 19) Setting | Must Trip frequency Magnitude. Frequency values shall be reported to 3 decimal places
| UF1_TRIP_T-SR-MIN | 180 | s |  | UF1_TRIP_T | UF Curve Trip Point UF1 (see Table 19) Setting | Must Trip Duration
| UF1_TRIP_T-SR-MAX | 1000 | s |  | UF1_TRIP_T | UF Curve Trip Point UF1 (see Table 19) Setting | Must Trip Duration
UF2 | UF2_TRIP_F-SR-MIN | 50 | Hz |  | UF2_TRIP_F | UF Curve Trip Point UF2 (see Table 19) Setting | Must Trip frequency Magnitude. Frequency values shall be reported to 3 decimal places
| UF2_TRIP_F-SR-MAX | 57 | Hz |  | UF2_TRIP_F | UF Curve Trip Point UF2 (see Table 19) Setting | Must Trip frequency Magnitude. Frequency values shall be reported to 3 decimal places
| UF2_TRIP_T-SR-MIN | 0.16 | s |  | UF2_TRIP_T | UF Curve Trip Point UF2 (see Table 19) Setting | Must Trip Duration
| UF2_TRIP_T-SR-MAX | 1000 | s |  | UF2_TRIP_T | UF Curve Trip Point UF2 (see Table 19) Setting | Must Trip Duration
P(f) Mode Select | PF_MODE_ENABLE-AS | ENABLED | Text | Required Tested Values: ENABLED/DISABLED | PF_MODE_ENABLE | frequency-Active Power Mode Enable | May be disabled only with aproval of Regional Balancing Authority
P(f )Deadband | PF_DBOF-SR-MIN | 0.017 | Hz |  | PF_DBOF | Overfrequency Droop dbOF Setting | Over Frequency deadband offset from nominal frequency in Hz Frequency values shall be reported to 3 decimal places
| PF_DBOF-SR-MAX | 1 | Hz |  | PF_DBOF | Overfrequency Droop dbOF Setting | Over Frequency deadband offset from nominal frequency in Hz Frequency values shall be reported to 3 decimal places
| PF_DBUF-SR-MIN | 0.017 | Hz |  | PF_DBUF | Underfrequency Droop dbUF Setting | Under Frequency deadband offset from nominal frequency in Hz Frequency values shall be reported to 3 decimal places
| PF_DBUF-SR-MAX | 1 | Hz |  | PF_DBUF | Underfrequency Droop dbUF Setting | Under Frequency deadband offset from nominal frequency in Hz Frequency values shall be reported to 3 decimal places
P(f) Droop Coefficient | PF_KOF-SR-MIN | 0.02 | unitless |  | PF_KOF | Overfrequency Droop kOF Setting | Over frequency per unit frequency change corresponding to a 1 per unit power change (frequency droop)
| PF_KOF-SR-MAX | 0.07 | unitless |  | PF_KOF | Overfrequency Droop kOF Setting | Over frequency per unit frequency change corresponding to a 1 per unit power change (frequency droop)
| PF_KUF-SR-MIN | 0.02 | unitless |  | PF_KUF | Underfrequency Droop kUF Setting | Under frequency per unit frequency change corresponding to a 1 per unit power change (frequency droop)
| PF_KUF-SR-MAX | 0.07 | unitless |  | PF_KUF | Underfrequency Droop kUF Setting | Under frequency per unit frequency change corresponding to a 1 per unit power change (frequency droop)
P(f) Open Loop Response Time | PF_OLRT-SR-MIN | 0.2 | s |  | PF_OLRT | P(f) Open Loop Response Time Setting | Open Loop Response time
| PF_OLRT-SR-MAX | 10 | s |  | PF_OLRT | P(f) Open Loop Response Time Setting | Open Loop Response time
UI Mode Select | UI_MODE_ENABLE-AS | ENABLED | Text | Required Tested Values: ENABLED/DISABLED | UI_MODE_ENABLE | N/A—AI is always on in IEEE Std 1547 BUT IEEE Std 1547.1 test says turn it off for some testing | Unintentional Islanding Mode (enabled/disabled). This function is enabled by default, and disabled only by request from the Area EPS Operator.
UI Methods Evaluated | UI_CAPABILITY-ER | UI_BLRC-UI_PCPST-UI_PHIT-UI_RMIP | Text | Value: UI_BLRC/UI_PCPST/UI_PHIT/UI_RMIP |  |  | Unintential Islanding methods supported Where multiple modes are supported separate with underscores. UI BLRC = Balanced RLC, UI PCPST = Powerline conducted, UI PHIT = Permissive Hardware-input, UI RMIP = Reverse/min relay. Methods other than UI BRLC may require supplemental comissioning tests.
Surge Protection / EMC | SURGE_LOC_CAT_EXPOSE-LEVEL | A-B-C_HIGH-C _LOW | Text | Value: A/B/C_HIGH/C_LOW |  |  | Surge Location Category / Exposure Level from IEEE Std C62.41.2, C62.45 and IEC 61000-4-5 (as applicable). DER requiring external surge devices to meet a specific rating may require supplementary review during commissioning testing
| EMC_IMMUN_LEVEL | PASS | Text | Value: PASS/FAIL | EMC_IMMUN_LEVEL | See IEEE Std 1547-2018 4.11.1 | EMC Immunity Level from IEEE Std C37.90.1. and C37.90.2.
Communication Protocols Evaluated | IEEE_2030_5-EVAL | TRUE | Boolean | Value: TRUE/FALSE; One or more protocols must be marked TRUE |  |  | "True" indicates IEEE 2030.5 functionality was evaluated.
| IEEE_1815-EVAL | TRUE | Boolean | Value: TRUE/FALSE; One or more protocols must be marked TRUE |  |  | "True" indicates IEEE 1815 functionality was evaluated.
| SUNSPEC_MODBUS_TCP-EVAL | TRUE | Boolean | Value: TRUE/FALSE; One or more protocols must be marked TRUE |  |  | "True" indicates SunSpec Modbus TCP functionality was evaluated.
| SUNSPEC_MODBUS_SERIAL-EVAL | TRUE | Boolean | Value: TRUE/FALSE; One or more protocols must be marked TRUE |  |  | "True" indicates SunSpec Modbus serial (RS-485) functionality was evaluated.
HVRT2 | OV2_RT_V-SR-MAX | [5 empty] | Ridethrough magnitude. Per unit value based on nameplate nominal voltage. (Voltage Base).
| OV2_RT_V-SR-MIN | 1.2 | V p.u. |  |  |  | Ridethrough magnitude. Per unit value based on nameplate nominal voltage. (Voltage Base).
| OV2_RT_T-SR-MAX | [5 empty] | Ridethrough maximum response time
| OV2_RT_T-SR-MIN | 0.16 | s |  |  |  | Ridethrough duration.
| OV2_RT_BEHAVIOR-SR | CTE | Text |  |  |  | DER operating mode
HVRT1 | OV1_RT_V-SR-MAX | 1.2 | V p.u. |  |  |  | Ridethrough magnitude. Per unit value based on nameplate nominal voltage. (Voltage Base).
| OV1_RT_V-SR-MIN | 1.1 | V p.u. |  |  |  | Ridethrough magnitude. Per unit value based on nameplate nominal voltage. (Voltage Base).
| OV1_RT_T-SR-MAX | 0.083 | s |  |  |  | Ridethrough maximum response time
| OV1_RT_T-SR-MIN | 12 | s |  |  |  | Ridethrough duration.
| OV1_RT_BEHAVIOR-SR | MC | Text |  |  |  | DER operating mode
LVRT3 | LV3_RT_V-SR-MAX | 0.5 | V p.u. |  |  |  | Ridethrough magnitude. Per unit value based on nameplate nominal voltage. (Voltage Base).
| LV3_RT_V-SR-MIN | [5 empty] | Ridethrough magnitude. Per unit value based on nameplate nominal voltage. (Voltage Base).
| LV3_RT_T-SR-MAX | 0.083 |  |  |  |  | Ridethrough maximum response time
| LV3_RT_T-SR-MIN | 1 | s |  |  |  | Ridethrough duration.
| LV3_RT_BEHAVIOR-SR | MC | Text |  |  |  | DER operating mode
LVRT2 | LV2_RT_V-SR-MAX | 0.7 | V p.u. |  |  |  | Ridethrough magnitude. Per unit value based on nameplate nominal voltage. (Voltage Base).
| LV2_RT_V-SR-MIN | 0.5 | V p.u. |  |  |  | Ridethrough magnitude. Per unit value based on nameplate nominal voltage. (Voltage Base).
| LV2_RT_T-SR-MAX | [5 empty] | Ridethrough maximum response time
| LV2_RT_T-SR-MIN | 10 | s |  |  |  | Ridethrough duration.
| LV2_RT_BEHAVIOR-SR | MO | Text |  |  |  | DER operating mode
LVRT1 | LV1_RT_V-SR-MAX | 0.88 | V p.u. |  |  |  | Ridethrough magnitude. Per unit value based on nameplate nominal voltage. (Voltage Base).
| LV1_RT_V-SR-MIN | 0.7 | V p.u. |  |  |  | Ridethrough magnitude. Per unit value based on nameplate nominal voltage. (Voltage Base).
| LV1_RT_T-SR-MAX | [5 empty] | Ridethrough maximum response time
| LV1_RT_T-SR-MIN | 20 | s |  |  |  | Ridethrough duration.
| LV1_RT_BEHAVIOR-SR | MO | Text |  |  |  | DER operating mode
HFRT1 | OF1_RT_V-SR-MAX | 65 | Hz |  |  |  | Ridethrough magnitude. Frequency values shall be reported to three decimal places.
| OF1_RT_V-SR-MIN | 63 | Hz |  |  |  | Ridethrough magnitude. Frequency values shall be reported to three decimal places.
| OF1_RT_T-SR-MAX |  | s |  |  |  | Ridethrough maximum response time
| OF1_RT_T-SR-MIN | 299 | s |  |  |  | Ridethrough duration.
| OF1_RT_BEHAVIORT-SR | MO_P(f) | Text |  |  |  | DER operating mode
LFRT1 | LF1_RT_V-SR-MAX | 57 | Hz |  |  |  | Ridethrough magnitude. Frequency values shall be reported to three decimal places.
| LF1_RT_V-SR-MIN | 50 | Hz |  |  |  | Ridethrough magnitude. Frequency values shall be reported to three decimal places.
| LF1_RT_T-SR-MAX |  | s |  |  |  | Ridethrough maximum response time
| LF1_RT_T-SR-MIN | 299 | s |  |  |  | Ridethrough duration.
| LF2_RT_BEHAVIOR-SR | MO_P(f) | Text |  |  |  | DER operating mode